## Slide 1: ERCOT System Protection Working Group
Bitter Creek 345kV trip March 21st, 2005

## Slide 2
ERCOT system one-line diagram

## Slide 3
Elm Creek
Graham DFR (TXU)
Mulberry Creek
LCRA Bitter Creek
138 kV
345 kV
Mulberry Creek East
Simple schematic diagram of substations & circuits involved
CB 5985
CB 5700 & 6005

## Slide 4
Fault on AEP 138kV line between Mulberry Creek and Elm Creek
Graham switching station (TXU) DFR shows low current remote fault on phase A
Bitter Creek DFR showed AG fault with fault current of around 590A on A phase (3Io = 410A)
Bitter Creek (LCRA) CB11480/11500 over-tripped
Over-trip due to carrier fail to block condition
Relay setting error for carrier start elements on TXU’s 345kV CB7010 terminal at Mulberry Creek
Event summary

## Slide 5: Event summary (contd.)
Mulberry Creek to Elm Creek 138kV line locked out on 1 operation
  Closed by SCADA after 3 minutes
  AEP personnel are investigating reclosing relay problem
Line was patrolled but no cause of fault was found
Bitter Creek 345kV breakers closed back after 2.5 minutes
LCRA owns the 345kV breakers and relaying at Bitter Creek
TXU owns the line and remote relay terminals (Mulberry Creek)
Notes: According to David Penney @ LCRA, Bitter Creek 345kV breakers opened at 11:00:25 and closed back at 11:03:01
According to Mark Chronister @ TXU, Mulberry Creek AutoXFMR CB5700 tripped at 11:00:28 and closed back at 11:05:41

## Slide 6: Graham switching station DFR
39 cycle clearing time; fault on A phase

## Slide 7
CB11500
CB11480
345 kV line to Mulberry Creek
LCRA Bitter Creek substation one-line diagram

## Slide 8: Findings & corrective actions
Bitter Creek (LCRA) over-tripped due to carrier fail to block condition at Mulberry Creek (TXU)
Relay setting error for carrier start elements on TXU’s 345kV CB7010 terminal at Mulberry Creek
The carrier start/stop ground overcurrent pickup levels at the TXU end were not properly coordinated with the settings for similar elements at the LCRA end
Mulberry Creek terminal settings were corrected
  To provide an appropriate pickup ratio between the Mulberry carrier ground start/block element and the Bitter Creek stop/trip element
  To ensure that carrier block element will reliably pick up before the carrier trip element does