## Slide 1: Communication with Backup Centers
John Adams
ROS – May 12, 2005

## Slide 2: ERCOT has a procedure in its EMMS group guiding switch to Backup
CONTACT EMMS Personnel on call
To move to the backup path, QSE’s must make configuration changes, so make sure they are ready before doing any switching.
Each QSE has 6 primary paths, three on ERPFEA/C and three on ERPFEB/D. If the QSE has a backup there will also be 6 paths for that site, these paths are usually removed from service. Refer to list below.
Remove all primary paths except the one that is oneline (path with solid green line).
Put in service all the backup paths.
Remove the primary path that is oneline. This will cause the RTU to fail to the left most, healthy path, which should be the first backup path.
Make sure you allow all the paths to attempt to scan.
If all paths fail, call for support.