J. Schmuck: I did not see any of AEP's Corpus area projects listed on the project status report.  The last I heard most of these were supposed to be finished about this time to allow the release of Barney Davis from RMR service.  What is the status of these projects?  Is the Nelson Sharpe substation project still scheduled for completion next year?

Ken D.: The projects listed in the report are only major projects (345 kV).  If we included every project the report would be too large.  The complete detailed workbook is available in the Operations and System Planning data area in the Transmission Project Information Tracking (TPIT) data folder.  I downloaded the file from that area released March 1 containing data as of February 1.  I filtered it with the South RPG, AEP TCC, Nueces and Kleburg Counties.  It details the projects underway near Corpus Christi.  It shows a projected in-service date of May 2006 for the Nelson Sharp project.  It also shows many other projects in the area.  New TPIT updates are due now and will be released June 1.

-----

M. Gaudi: On sheet 7, do the 4,016 Wind MW applications include the wind farms with signed interconnections also shown on the same sheet?

Ken D.: Yes they are included.

-----

G. Pressler: What about Elm Creek switching station? I don't see it in the report.

Ken D.: This list is only 345 kV projects.  If you need details you should use the full TPIT workbook posted in the Operations and System Planning data area.  To produce this table we filtered on “Service Level kV” equal to 345 and sorted on in-service date.  CPS entered 345/138 in this column.  Therefore this project did not show up in the filtered version.  Not sure why you are showing 345/138 kV because only 345 kV work is being done at this time.  Suggest correcting this situation in the next TPIT submission to Michelle Pair.  Only a single kV should be in this column.

-----

J. Armke: 1. On page 8, roughly what is the latest target date for achieving the referenced 755 MW wind export capability for the McCamey area?

Ken D. : AEP TCC expects to have a major portion of the additional reactive including dynamic installed by 3rd QTR 2005 with additional dynamic reactive installed by 2nd QTR 2006.  TPIT workbook should provide latest projects details and projected in-service dates.  Next update is expected to be posted June 1.

-----

J. Armke: 2. What were the "lessons learned" from the April 28 McCamey generation event?

Ken D. : Wind Farm operators and Transmission operators need to better coordinate reactive devices/controls to improve production.

-----

J. Armke: 3. Why is there a concern regarding a Transient Voltage Dip in Corpus Christi?

Ken D.: Refer to attached ERCOT Board document from September 2004.  Contract has been completed and study is well underway.  You might want to visit with Bridget Knower from Flint Hills at the ROS meeting.

-----

J. Armke: 4. On page 9, please re-state what ERCOT is expecting each TO to do to develop "input into other locations addition for UVLS" that is due to ERCOT on June 1.

Ken D.: Suggest reviewing with your staff that attended the meeting.  I believe Reza E. was there most of the time.  ERCOT Staff feels that consideration should be given to implementing automatic UVLS within all load serving entities at the following locations:

Lower Rio Grande Valley      maintain at 25% of Load

Laredo                       maintain at 25% of Load

Houston                      increase to 25% of Load

Dallas-Ft. Worth             25% of Load

San Antonio                  25% of Load

Austin                       25% of Load

Bryan/College Station        25% of Load

Midland/Odessa               25% of Load

Corpus Christi               25% of Load

San Angelo                   25% of Load

Abilene                      25% of Load

Waco                         25% of Load

Killeen/Temple               25% of Load

Tyler                        25% of Load

We requested a response from TO's for each of these areas by June 1.  Also, if they did not feel UVLS was necessary to provide the basis.

-----

Many stakeholders: Can you add an RMR Unit Status with target exit dates to the report?

Ken D.: We will add this to the May report and future reports.

-----

S. Helyer: You might want to consider providing some feedback on any decisions that come out of today's North Texas Regional Planning Group meeting.  I'm not looking for a big summary, but just the key decisions as I can read the presentations myself.  I think some folks, like me today, cannot always make the regional planning group meetings and some very, very brief feedback would be helpful during the ROS meetings.

Ken D.: Summary of NRPG is for the May report to ROS.  More info will be coming out to NRPG email list.

-----