ROS Summary Report to TAC for June 2, 2005

# At this time, ROS has no voting items recommended for TAC Approval.

PRS remand of PRR 586 – SCE Performance and Regulation Cost Re-allocation - to ROS to frame the issue, determine any unintended consequences, and revise as needed. Prior to ROS, the PDCWG will have an open meeting on Tuesday, June 14, 2005 from 9:30 am to 4:00 pm in room 206B at the Austin Met Center.  The ROS response to PRS is due by the July 21st PRS meeting.

Operating Guide Revisions in comment period:

OGRR 163 - State Estimator Requirements  – TAC action item assigned to ROS. This OGRR includes sections 5 and 6 from the “State Estimator Observability and Redundancy Requirements” document, placed in the appropriate Operating Guide section as determined by OGRTF, outlining ERCOT’s requirements and exception process.  Comments regarding the exception process and timeline were posted on April 20th.

OGRR 164 – Responsive Reserve MW Limit – Addresses Potomac Economics’ Recommendation No. 13 which changes the limit of RRS on an individual Generation Resource from 20% of Net Generation Capability to 20% of Net Generation Capability or 50MW, whichever is greater. This is OGRR 161 revisited and should come to the July TAC meeting for consideration.

OGRR 165 – Unit Telemetry Requirement – Addresses Potomac Economics’ Recommendation No. 14 meant to improve ERCOT’s wholesale market design.  This recommendation states that ERCOT should monitor a QSE’s ability to meet its Responsive Reserve Obligation in real-time.  Currently, capacity is monitored, but a unit’s ramp rate is not monitored.  This revision will incorporate a unit’s ramp rate and Automatic Generation Control (AGC) status in the data provided to ERCOT.

##### OGRR 166 – Double Circuit Contingencies - ERCOT currently deploys energy as if all double circuits would cause cascading outages 24 hours a day, 7 days a week. This OGRR would allow ERCOT to continue counting double circuits as a single contingency when weather or studies dictate and always have sufficient generation to redispatch for security, but would save Congestion costs under normal circumstances.

OGRR 167 – LaaR Underfrequency Relay Interruption Time - Adds LaaR interruption total time limit of 30 cycles including all relay and breaker interruption times.

Current ROS Activities:

- Reactive Testing Compliance

- QSE / TO Back-up Center Communications

- Annual Underfrequency Load Shedding results are being compiled