May Report

To

Technical Advisory Committee

Reliability and Operations Subcommittee

Prepared by ERCOT Transmission Services

Major transmission projects completed

| Project Title | Project Description | Transmission Owner | Actual In-Service Date | Service Level kV |
| --- | --- | --- | --- | --- |
| Eagle Mountain 345 kV breakers | Install two 345 kV breakers | TXU Electric Delivery | Apr-05 | 345 |
| Roanoke Switch 345/138 kV autotransformer | Install (2nd) 345/138 kV autotransformer (600 MVA) at Roanoke Switch | TXU Electric Delivery | Mar-05 | 345 |
| Watermill - Tricorner 345 kV line | Upgrade Watermill - Tricorner 345 kV line | TXU Electric Delivery | Feb-05 | 345 |
| Obrien 345/138 kV autotransformer | Added third 345/138 kV, 400MVA autotransformer (A3) @Obrien | CNP | Jan-05 | 345 |
| Red Creek, add 100 MVar shunt reactor | The addition of 100 MVAR shunt reactor at the 345 KV Red Creek | AEP/TNC | Dec-04 | 345 |
| Mulberry Creek, add 36 MVar shunt reactor | The addition of 36 MVAr shunt reactor on the autotransformer tertiary at Mulberry Creek. | AEP/TNC | Dec-04 | 345 |
| Oasis Switching Station | Built Oasis 345 kV Substation and looped ckt.99 Dow-WAP and ckt.99 Dow-PHR into the new substation. | CNP | Nov-04 | 345 |
| Tomball - Jewett ckt.1 | Verified tie line from Tomball to TXU tie point conductor clearance to increase thermal ratings to 1450 MVA | CNP | Nov-04 | 345 |
| W.A. Parish - Oasis ckt.99 | Bundled 345 kV W.A. Parish - Oasis Ckt.99. Partially rebuilt 69 kV ckt.53 from Karsten to Manvel Tap | CNP | Oct-04 | 345 |
| Twin Buttes, add SS with 345/138 kV autotransformer | Twin Buttes 345/138 kV substation cut-in to the Big Lake to SAPS 138 kV line and re-build of Twin Buttes to SAPS 138 kV line | LCRA/AEP | Oct-04 | 345 |
| W.A. Parish - Obrien ckt.98 | Raised conductors and upgraded substation equipment to increase thermal ratings | CNP | Oct-04 | 345 |
| Roans Prairie - King ckt.75 | Verified conductors clearance to increase thermal ratings. | CNP | Sep-04 | 345 |
| T.H.Wharton - Obrien ckt.98 | Verified conductors clearance to increase thermal ratings. | CNP | Sep-04 | 345 |
| Tomball - King ckt.74 | Verified conductors clearance to increase thermal ratings. | CNP | Sep-04 | 345 |
| Gibbons Creek - Roans Prairie ckt.75 | Verified conductors clearance to increase thermal ratings. | CNP, TMPA | Sep-04 | 345 |
| T.H.Wharton - Jewett ckt.1 | Raised conductors to increase thermal ratings | CNP, TXU | Sep-04 | 345 |
| Tomball - Jewett ckt.1 | Verified conductors clearance to increase thermal ratings. | CNP, TXU | Sep-04 | 345 |
| T.H. Wharton 345/138 kV autotransformer | Replaced 400 MVA autotransformer (A1) @T.H. Wharton with 800MVA auto | CNP | Jun-04 | 345 |
| W.A. Parish - Obrien ckt.99 | Raised conductors and upgrade substation equipment to increase thermal ratings | CNP | Jun-04 | 345 |
| Jeanetta 345/138 kV autotransformer | Replaced failed 600 MVA autotransformer (A3) @Jeanetta | CNP | May-04 | 345 |
| W.A. Parish - Dow ckt.99 | Raised conductors and upgrade Dow substation equipment to increase thermal ratings | CNP | May-04 | 345 |
| Sargent Rd. 345/138 kV autotransformer | Install a 600 MVA 345/138 kv autotransformer at Sargent Rd. | TXU Electric Delivery | Apr-04 | 345 |
| Everman 345/138 kV autotransformer | Install (3rd) 345/138 kV autotransformer (600 MVA) at Everman | TXU Electric Delivery | Apr-04 | 345 |
| Royse 345/138 kV autotransformer | Replace a 450 MVA 345/138 kV autotransformer at Royse with a 600 MVA autotransformer | TXU Electric Delivery | Mar-04 | 345 |
| Cedar Bayou - North Belt ckt.99 | Upgraded limiting equipment at Cedar Bayou to increase thermal ratings. | CNP | Feb-04 | 345 |
| Chambers - King ckt. 97 | Upgraded limiting equipment at King to increase thermal ratings. | CNP | Feb-04 | 345 |
| Zorn Auto | Replace the 478MVA Zorn Auto 2 with a 600MVA auto (7045-7180) temporarily | LCRA | Jan-04 | 345 |
| Zorn Auto | Replace the 478MVA Zorn Auto 2 with a 600MVA auto (7045-7180) | LCRA | Jan-04 | 345 |

Status of major transmission projects

| Project Title | Project Description | Transmission Owner | Projected In-Service Date | Service Level kV | Location County |
| --- | --- | --- | --- | --- | --- |
| Anna 345/138 kV autotransformer | Install a (2nd) 345/138 kV autotransformer (600 MVA) at Anna | TXU Electric Delivery | May-05 | 345 | COLLIN |
| Lake Creek second 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer | TXU Electric Delivery | May-05 | 345 | MCLENNAN |
| Martin Lake 345 kV breakers | Install two 345 kV bus tie breakers | TXU Electric Delivery | May-05 | 345 | RUSK |
| Monticello 345 kV breaker | Install one 345 kV bus tie breaker | TXU Electric Delivery | May-05 | 345 | TITUS |
| Watermill - Cedar Hill (2nd) 345 kV circuit | Install Watermill - Cedar Hill (2nd) 345 kV circuit | TXU Electric Delivery | May-05 | 345 | DALLAS |
| Cedar Bayou 345/138 kV autotransformer | Add fourth 345/138 kV, 800MVA autotransformer (A4) @Cedar Bayou and reconnect third auto (A3) to the west bus, parallel to A1 & A2 | CNP | Jun-05 | 345 | HARRIS |
| Salem 345/138 kV autotransformer upgrade | Upgrade Salem 345/138 kV autotransformer capacity to 672 MVA | LCRA | Jun-05 | 345 | WASHINGTON |
| Kendall 345/138 kV autotransformer # 2 | Install a second 345/138 kV autotransformer at the Kendall substation | LCRA | Jun-05 | 345 | KENDALL |
| Watermill - W. Levee (2nd) 345 kV circuit | Install Watermill - W. Levee (2nd) 345 kV circuit | TXU Electric Delivery | Oct-05 | 345 | DALLAS |
| Bellaire 345/138kV autotransformer | Upgrade Autotransformer (A1) position to increase thermal ratings | CNP | Nov-05 | 345 | HARRIS |
| Bellaire 345/138kV autotransformer | Upgrade Autotransformer (A4) position to increase thermal ratings | CNP | Nov-05 | 345 | HARRIS |
| Rio Hondo, add 345/138 kV auto | Rebuild La Palma to Rio Hondo 138 kV with 2-795 ACSS, double circuit capable and add 345/138 kV autotransformer at Rio Hondo | AEP/TCC | Apr-06 | 345 | CAMERON |
| Pecan Creek 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at Pecan Creek | TXU Electric Delivery | May-06 | 345 | BELL |
| Venus - Sherry 345 kV line | Construct Venus - Sherry 345 kV line | TXU Electric Delivery | May-06 | 345 | ELLIS |
| W. Levee - Norwood 345 kV line | Construct W. Levee - Norwood 345 kV line | TXU Electric Delivery | May-06 | 345 | DALLAS |
| Venus - Liggett 345 kV line | Construct Venus - Liggett 345 kV line | TXU Electric Delivery | May-06 | 345 | ELLIS |
| Venus - Johnson Switch 345 kV line | Upgrade existing 345 kV line | TXU Electric Delivery | May-06 | 345 | ELLIS |
| Valley 345/138 kV autotransformer | Replace existing 450 MVA 345/138 kV autotransformer with a 600 MVA autotransformer | TXU Electric Delivery | May-06 | 345 | FANNIN |
| Jewett - TH Wharton 345 kV line upgrade | Upgrade tie lines from Jewett to TXU Electric Delivery tie point to increase thermal ratings to 1450 MVA or above. | TXU Electric Delivery | May-06 | 345 | LEON |
| Jewett - Tomball 345 kV line upgrade | Upgrade tie lines from Jewett to TXU Electric Delivery tie point to increase thermal ratings to 1450 MVA or above. | TXU Electric Delivery | May-06 | 345 | LEON |
| T.H.Wharton - Jewett ckt.1 | Upgrade tie lines from TH Wharton to TXU tie point to increase thermal ratings to 1450 MVA by raising conductors and upgrading limiting equipment at TH Wharton | CNP | May-06 | 345 | HARRIS |
| Nelson Sharpe, add 345/138 kV autotransformer | Construct Nelson Sharpe 345/138 kV substation in the Lon Hill to Rio Hondo 345 kV line and add a phase-shifting transformer at Nelson Sharpe in Davis 138 kV line | AEP/TCC | May-06 | 345 | KLEBERG |
| Zorn Auto | Replace the 600MVA Zorn Auto 2 with a 478MVA auto (7045-7180) | LCRA | Jun-06 | 345 | GUADALUPE |
| Clear Springs | Add a new 345/138 kV 478 MVA auto-transformer at the Clear Springs substation(7050). The existing 345 kV bus at the Clear Springs will be converted from a ring bus configuration to a double-bus double-breaker configuration. Upgrade the 7.2-mile Clear Springs(7680)-Geronimo(7604)-Seguin(7228) 138 kV transmission line (T-264) from 336 ACSR to Bundled 795 ACSR double circuit capable. Upgrade the 7.2-mile Clear Springs(7680)-Freiheit(7462)-Hortontown(7175)-Comal(7176) 138 kV transmission line (T-264, T-394, and T-119) from 336 ACSR to Bundled 795 ACSR double circuit capable. | LCRA | Jun-06 | 345 | GUADALUPE |
| Kendall-CPS Cagnon 345-kV line | Construct a 345 kV bundled 1590 ACSR line (approximately 45 miles) between Kendall (7046) and Cagnon (5056) | LCRA / CPS | Jun-06 | 345 | BEXAR |
| Skyline - Replace 345kV Autotransformer #2 & #4 | Replace the two 480 MVA autotransformers(#2 & #4) with one 600 MVA autotransformer. | CPS | Jul-06 | 345 | BEXAR |
| Elm Creek Substation | Install new 345 kV switching station at the intersection of the existing 345kV lines from STP-Skyline, STP-Hill Country, and both lines from Marion to San Miguel. | CPS | Oct-06 | 345 | GUADALUPE |
| Jacksboro Switch - W. Denton 345 kV line | Construct Jacksboro Switch - W. Denton 345 kV line | TXU Electric Delivery | Dec-06 | 345 | JACK |
| Sandow 345/138 kV autotransformer | Install second 345/138 kV autotransformer | TXU Electric Delivery | Dec-06 | 345 | MILAM |
| Odessa EHV 345/138 kV 300 MVA autotransformer replacement | Replace existing 300 MVA 345/138 kV autotransformer with a 450 MVA autotransformer | TXU Electric Delivery | Dec-06 | 345 | ECTOR |
| Sandow 345/138 kV autotransformer | Install second 345/138 kV autotransformer | TXU Electric Delivery | Dec-06 | 345 | MILAM |
| Paris Switch - Anna 345 kV line | Construct Paris Switch - Anna 345 kV line | TXU Electric Delivery | Dec-06 | 345 | LAMAR |
| WAP 345 kV sub. | Upgrade fault duty rating of WAP 345 kV to at least 56 kA | CNP | Dec-06 | 345 | FORT BEND |
| Smithers 345 kV sub. | Upgrade fault duty rating of Smithers 345 kV to at least 52 kA | CNP | Dec-06 | 345 | FORT BEND |
| STP - Dow ckt.18 and ckt.27 | Replace 2000 Amp equipment on both circuits from STP to DOW. | CNP | Dec-06 | 345 | MATAGORDA |
| DeCordova - Benbrook 345 kV line upgrade | Upgrade capacity of line | TXU Electric Delivery | May-07 | 345 | HOOD |
| DeSoto 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at DeSoto | TXU Electric Delivery | May-07 | 345 | DALLAS |
| Plano Tennyson 345/138 kV autotransformer | Install a 600 MVA 345/138 kV autotransformer at Plano Tennyson | TXU Electric Delivery | May-07 | 345 | COLLIN |
| Trinidad - Richland 345 kV line | Upgrade Trinidad - Richland 345 kV line | TXU Electric Delivery | May-07 | 345 | HENDERSON |
| Venus - Cedar Hill 345 kV line | Upgrade existing 345 kV line | TXU Electric Delivery | May-07 | 345 | ELLIS |
| Spruce to Skyline 345kV 2nd Circuit | Build 2nd 345 kV line from Spruce to Skyline substation | CPS | Jun-07 | 345 | BEXAR |
| Second Whitney 345/138 Autoitransformer | Install second 450MVA 345/138KV auto at Whitney | Brazos | Jun-08 | 345 | BOSQUE |
| Hillje Switching Station | Build a new 345 kV Hillje substation. Loop ckt.1 STP-Holman into the new substation. | CNP | Dec-08 | 345 | WHARTON |
| STP - Hillje ckt. | Build new 345 kV line from STP to Hillje. | CNP | Dec-08 | 345 | MATAGORDA |
| WAP - Hillje ckt. | Build new 345 kV double circuit line from WA Parish to Hillje. | CNP | Dec-08 | 345 | FORT BEND |
| Increase CNP 345/138 kV autotransformer capacity | Add several 800 MVA autotransformers in the CNP transmission system | CNP | Dec-08 | 345 | HARRIS/CHAMBERS/FORT BEND/GALVESTON/BRAZORIA |
| WA Parish - Bellaire ckt 50 | Raise conductors to increase thermal ratings | CNP | Dec-08 | 345 | FORT BEND |
| Smithers - Bellaire ckt.98 | Raise conductors to increase thermal ratings | CNP | Dec-08 | 345 | FORT BEND |
| West Denton - NW Carrollton 345 kV circuit | Add second Circuit from West Denton to NW Carrollton | TXU Electric Delivery/TMPA | May-09 | 345 | DENTON |
| Skyline - Install a third 345kV Autotransformer | Install one 600 MVA autotransformer. | CPS | May-09 | 345 | BEXAR |
| Second Concord 345/138 Autotransformer | Install second 300MVA 345/138KV auto at Concord | Brazos | Jun-09 | 345 | JOHNSON |
| Cagnon to Hillcountry 345kV 2nd Circuit | Build 2nd 345 kV line from Cagnon to Hill Country substation | CPS | Jun-09 | 345 | BEXAR |
| Hill Country to Skyline 345 kV 2nd Circuit | Build 2nd 345 kV line from Hillcountry to Skyline substation | CPS | Jun-09 | 345 | BEXAR |
| Dansby to Twin Oak 345 kV | Design and build a double circuit 345 that will tie into the existing TMPA Gibbons to Twin Oaks line | BTU | Jul-09 | 345 | BRAZOS |
| 2nd Lewisville Auto | Install (2nd) 345/138 kV autotransformer at Lewisville station | Brazos | Dec-09 | 345 | DENTON |
| Laredo Lobo, build 345 kV for 675MVA autotransformer | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and conver | AEP/TCC | Mar-10 | 345 | WEBB |
| Laredo Lobo to San Miguel, build 345 kV line | Construct new Laredo Lobo to San Miguel 345 kV line with Laredo Lobo 345/138 kV substation where the existing Falfurrias to Laredo 138 kV and the Freer to Laredo 69 kV transmission lines cross Highway 59, rebuild Laredo Lobo to Laredo 138 kV line and conver | AEP/STEC | May-10 | 345 | WEBB |
| Liggett - Trinity Switch 345 kV line | Construct Liggett - Trinity 345 kV line | TXU Electric Delivery | May-10 | 345 | DALLAS |
| Trinity Switch 345/138 kV autotransformer | Create Trinity Switch and install a 600 MVA 345/138 kV autotransformer | TXU Electric Delivery | May-10 | 345 | TARRANT |
| Hutto Switch - Salado Switch 345 kV line | Construct Hutto Switch - Salado Switch 345 kV line | TXU Electric Delivery | May-10 | 345 | WILLIAMSON |
| Hutto Switch 345/138 kV autotransformer | Create 345 kV switching station and install a 345/138 kV autotransformer | TXU Electric Delivery | May-10 | 345 | WILLIAMSON |
| Zorn/Clear Springs-Harris Branch-Hutto Switch 345-kV line | Construct a 345 kV DC 2x1590 ACSR line between Zorn/Clearsprings and Hutto Switch and other ONCOR and AE projects | LCRA | Jun-10 | 345 | WILLIAMSON |
| Harris Branch 345/138kV autotransformer | Install a 345/138kV autotransformer at Harris Branch substation | Austin Energy | Dec-10 | 345 | TRAVIS |
| Harris Branch 345/138kV autotransformer & Harris Branch 138kV circuit to East and Techridge Substation. | Install a 345/138kV autotransformer at Harris Branch substation. Cut-in the existing East to Techridge 138kV circuit to establish the 138kV East to Harris and 138kV Harris to Techridge circuits | Austin Energy | Dec-10 | 345 | TRAVIS |
| Frontera, add SS with 345/138 kV autotransformer | Addition North Edinburg to Frontera to South McAllen 345 kV line with bundled 1590 ACSR conductor and double circuit capable structures and 345/138 kV substation at Frontera | AEP/TCC | May-11 | 345 | HIDALGO |
| Laredo Lobo to Rio Bravo, new 345 kV line | Construct 345 kV line from Highway 59 to Rio Bravo to Frontera and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer | AEP/TCC | May-11 | 345 | WEBB |
| Frontera to Rio Bravo, new 345 kV line | Construct 345 kV line from Highway 59 to Rio Bravo to Frontera and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer | AEP/TCC | May-11 | 345 | WEBB |
| Rio Bravo, 138 kV SS with 345/138 kV autotransformer | Construct 345 kV line from Highway 59 to Rio Bravo to Frontera and add 345/138 kV substation at Rio Bravo with 345/138 kV autotransformer | AEP/TCC | May-11 | 345 | WEBB |
| North McCamey to Twin Buttes 345 kV Line | 12/02 plan recommends the construction of a 345kV 2x1590 ACSR line between North McCamey and Twin Buttes | LCRA/AEP | Jan-12 | 345 | UPTON |
| North McCamey - Odessa 345 kV Line | 12/02 plan recommends the construction of a 345 kV 2x1590 ACSR line between North McCamey and Odessa and 2x600 MVA autotransformers at North McCamey | LCRA/AEP | Jan-12 | 345 | UPTON |
| North McCamey 345/138 kV autotransformer | Recommends the addition of a 345/138kV autotransformer North McCamey | LCRA/AEP | Jan-12 | 345 | UPTON |
| Frontera to South McAllen 345 kV line | Construct a 345 kV transmission line from Frontera to South McAllen. | LCRA/AEP | May-15 | 345 | HIDALGO |
| Rio Hondo to Ranchito, new 345 kV line | Construct 345 kV line from Rio Hondo to Ranchito and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer. Build 345 kV line | AEP/TCC |  | 345 | CAMERON |
| Ranchito, new SS with 345/138 kV autotransformer | Construct 345 kV line from Rio Hondo to Ranchito and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer. Build 345/138/69 kV station and autotransformer | AEP/TCC |  | 345 | CAMERON |
| Ranchito to South McAllen, new 345 kV line | Construct 345 kV line from Rio Hondo to Ranchito and add 345/138/69 kV substation adjacent to existing Cavazos 69 kV substation with 600 MVA 345/138 kV autotransformer. Build 345/138/69 kV station and autotransformer | AEP/TCC |  | 345 | CAMERON |
| South McAllen, new SS with 345/138 kV autotransformer | Construct a 345 kV substation south of South McAllen cut into the South McAllen to Hidalgo 138 kV line and install a 345/138 kV autotransformer | AEP/TCC |  | 345 | HIDALGO |
| Loma Alta - Ranchito or la Palma 345-kV line | Install 345-kV line from Loma Alta to La Palma or Ranchito | BPUB |  | 345 | CAMERON |
| Loma Alta - Rio Hondo 345-kV line | Install 345-kV line from Loma Alta to Rio Hondo | BPUB |  | 345 | CAMERON |
| Loma Alta 345kV station and autotransformer | Construct a 345 substation and connect to the existing Loma Alta 138 substation. | BPUB |  | 345 | CAMERON |
| Sandow - Temple Switch 345 kV line | Upgrade Sandow - Temple Switch 345 kV line | TXU Electric Delivery |  | 345 | MILAM |

Status of active generation interconnection requests

| PUBLIC PROJECTS |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- |
| INR # | SiteName | County |  | Region | Fuel | In Service Date | MW into Grid | Notes |
| 05INR0014 | Sun Substation | Scurry |  | West | Gas | May-05 | 0 |  |
| 04INR0015 | Maryneal (Buffalo Gap) | Taylor |  | West | Wind | Sep-05 | 240 | 120 MW in 2005, 120 MW in 2006 |
| 04INR0020 | WKN Wind 1 Snyder | Scurry |  | West | Wind | Dec-05 | 61 |  |
| 05INR0010 | Jack County Generation Facility | Jack |  | North | Gas | Dec-05 | 700 | testing 6/1/05, commercial 12/1/05 |
| 06INR0008 | Big Spring Carbon Plant | Howard |  | West | Waste heat | Apr-06 | 12 |  |
| 03INR0034 | Silver Star Project | Erath |  | West | Wind | Jun-06 | 60 |  |
| 05INR0018 | Horse Hollow | Taylor |  | West | Wind | Jun-06 | 347 | 220 MW by 7/1/05, 127 MW by 1/06 |
| 05INR0015 | Gulf Wind | Kenedy |  | South | Wind | Jul-06 | 200 |  |
| 06INR0016 | Dow 9 | Brazoria |  | South | NG | Oct-06 | 0 |  |
| 01INR0028 | Orion Delaware Mountain Wind Farm | Culberson |  | West | Wind | Dec-07 | 175 |  |
| 08INR0002 | Sandow 5 | Milam |  | North | Lignite | Jan-08 | 0 | Cancelled |
| 06INR0006 | Cobisa-Greenville | Hunt |  | North | Gas | May-08 | 1,750 |  |
| 09INR0002 | J K Spruce 2 | Bexar |  | South | Coal | Aug-09 | 750 |  |
| 10INR0002 | Hugo Plant | Choctaw, OK |  | North | Coal | Dec-10 | 500 |  |
|  |  |  |  |  | Totals |  | 4,795 |  |
| PROJECTS INTO OPERATION |  |  |  |  |  |  |  |  |
| INR # | SiteName | County |  | Region | Fuel | In Service Date | MW into Grid |  |
| 05INR0013 | Battleground 4 | Harris |  | South | NG | May-05 | 66 |  |
| ACTIVE GENERATION INTERCONNECTION REQUESTS BEING PROCESSED |  |  |  |  |  |  |  |  |
|  |  |  | North | South | West | Total |  |  |
| Security Screening Study |  |  | 1 | 1 | 3 | 5 |  |  |
| SSS Completed |  |  | 1 | 2 | 8 | 11 |  |  |
| Full Interconnect Study |  |  | 7 | 5 | 8 | 20 |  |  |
| FIS Completed |  |  | 1 | 0 | 3 | 4 |  |  |
| Interconnect Agreement Completed (Includes public letters) |  |  | 3 | 3 | 7 | 13 |  |  |
| Capacity for Grid, MW |  |  | 4,549 | 2,660 | 5,740 | 12,949 |  |  |
| Wind MW (under development) |  |  | 240 | 1,360 | 4,553 | 6,153 |  |  |

Studies completed or underway

- 2006 DFW/NE congestion relief study is complete. The plan is to complete the report in June and report it to TAC in July.

- 2009 DFW/NE Study Scope is being developed with stakeholder input.

- Internal efforts are ongoing to determine the fidelity of and best practices in planning for the generator Net Dependable Capability Testing Data that is reported to ERCOT compliance.

- Dynamics WG 2005 flat start base case tuning incorporating wind farm models

- LAAR  models for dynamic studies

- Steady State WG Data 2004 Set A & B base cases were updated and posted on the ERCOT website at the end of May

- The next Steady State WG base case and network model branch data comparison will be conducted on July 1

- A Steady State WG base case and network model transformer rating comparison will be conducted in June

Studies underway or planned to be started within Transmission Services

- Transient Voltage Dip analysis of the Corpus Christi area, work performed by Siemens/PTI in cooperation with Flint Hills, AEP TCC and ERCOT System Planning

- Stability load modeling project- Phase II (EPRI Solutions)

- Continuing support of Utility Wind Interest Group (UWIG) wind farm stability modeling effort

- PH Robinson RMR exit strategy

- Annual Survey of Critical Voltage Stability Events (reliability/security protected information)

- Annual Survey of Critical Transient Stability Events (reliability/security protected information)

- Dynamic limit evaluation of 2005 CSC/CM zonal transfers

- Support for the ERCOT Bryan/College Station study continues.  Once the topology has been finalized, a voltage study will be performed to quantify how the final study Option impacts voltage in the area.

- Laredo Must Run Alternative RFP issued.  Bids due 7/15/2005.

Studies that have been completed by Transmission Services and posting location

- Completed Regional Transmission Project Planning Group Peer Review and Acceptance of Clear Springs project to place a new 345/138 kV autotransformer at Clear Springs building a breaker and a half 138 kV station, and upgrading two 138 kV lines

- The 2005 Future Year short circuit base case data for the years 2006 to 2009 was due June 3rd, 2005.  The first Pass of the data will be completed once all of the data is received from the TDSPs on SPWG, since not all of it was received by the deadline.  TDSPs that did not meet the deadline have been notified.

- The revised Hays SPS is currently under ERCOT review.  Once all questions and concerns have been addressed by LCRA, the SPS should be approved.

- The recently submitted document from TXU ED containing new SPS’s (Hackberry and Commerce Switch) and several modifications to existing SPS’s is under ERCOT review and has not yet been approved.  Some of these modifications may have been applied in the field.  Operation of these modified SPS’s without ERCOT’s approval could be considered a misoperation and/or non-compliance with ERCOT procedures.

Upcoming Events

- July 15 - Meeting to review BM Davis and PH Robinson  RMR Exit Strategies

- July 6 & 7 – NERC PC TIS Meeting

Other Issues

- Responding to NERC recommendations ROS Dynamics WG will simulate an actual event to test dynamic models.  DWG is reviewing an event to assess its suitability to the NERC recommendation scope

- NREL is willing to perform stability studies together with ERCOT System Planning to validate the dynamic models of wind farm, subject to the availability of disturbance data for a transient event in the West Texas network

- Some SSWG members seem to perform more base case data verification than others which leads to a disparity in data accuracy and increased resources to resolve

NERC Phase III and IV Draft Standards:

Version 0 standards approved by NERC in February, 2005, did not include several important standards referred to as “Phase III and IV Planning Standards.”  There are 42 standards in this area which includes issues beyond planning, for example:

Black Start Capability

Disturbance Monitoring and Reporting

Generation and Transmission System Modeling, and

System Protection and Controls.

ERCOT encourages all of its members to comment on these and other standards.  In addition to ERCOT (i.e., the Regional Organization - RRO), these standards will affect Transmission Operators, Generator Owners, Transmission Owners, Transmission Planners, Distribution Providers, and Load Serving Entities.

Comments on the draft standards are due on June 13, 2005.  The comment form is found at www.nerc.com/~filez/standards/Phase-III-IV.html.

Interesting observations

- The change to Net Dependable Capability (NDC) values as Pmax of generating units in the latest network base cases (being created in 2005 for the year 2006 and beyond) will require that the dynamic data be tuned such that the numerical relationship between Pmax and Pgen does not create errors during dynamic simulations.  DWG members and ERCOT System Planning are working together to develop a process to adopt these changes

- Mothball/decommission of generation is reducing voltage stability margins

Future issues

- Developing/applying accurate load models for dynamic studies

- Update/verify wind farms models for dynamic studies

- Developing/applying accurate generator reactive capability curves

- Development of Combined Cycle Stability Models postponed to 2006 due to budget reduction, will be included in 2006 budget submission

Generation Currently Under RMR Contract in ERCOT (as of 6/1/05)

| Unit | Capacity (Net) | RMR Contract Status | Contract Date | Current Anticipated Exit Date |
| --- | --- | --- | --- | --- |
| BM Davis 2 | 356 | Under Contract | 1/1/05-12/31/05 | Under Review |
| JL Bates 1 & 2 | 183 | Under Contract | 1/1/05-12/31/05 | 3Q 2006 |
| La Palma 4, 5, 6, &7 | 249 | Under Contract | 1/1/05-12/31/05 | 1Q 2006 |
| Laredo 1, 2, & 3 | 172 | Under Contract | 1/1/05-12/31/05 | 3Q 2010 |
| PH Robinson 2 | 461 | Under Contract | 5/17/05-5/16/06 | Under Development |
| Total MW Under RMR: | 1,421 |  |  |  |

Transmission Project Summaries