## ERCOT Operations Report

## ROS & OWG

## May 2005

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 5/1/2005 0:09 | 60.103 | 23635 | -547 | 929 | -820 (-420) |
| 5/2/2005 7:25 | 60.109 | 28045 | -970 | 123 | Steel mill activity |
| 5/4/2005 23:53 | 60.187 | 25421 | -582 | 207 | -870 (-350) |
| 5/5/2005 5:59 | 60.117 | 25252 | -914 | 829 | 2450 (450) |
| 5/19/2005 16:05 | 60.101 | 46639 | -765 | 120 | Non conforming load |
| 5/20/2005 19:09 | 60.144 | 47802 | -848 | 73 | Held Interval |
| 5/21/2005 1:05 | 60.187 | 32199 | -132 | 21 | Figure 1 |
| 5/21/2005 1:25 | 60.108 | 31539 | -182 | -224 |  |
| 5/26/2005 1:13 | 60.120 | 30979 | -623 | 67 |  |
| 5/26/2005 2:06 | 59.872 | 29767 | 414 | 273 |  |
| 5/26/2005 2:57 | 60.118 | 28832 | -624 | 107 |  |
| 5/28/2005 11:15 | 60.102 | 35350 | 118 | 170 | Short event. Load trending upward but dips 11:15 – 11:20 |

| Disturbance Data |  | MW Lost |
| --- | --- | --- |
| 5/2/2005 11:33 | 59.888 | 320 - 1 trip + 1 runback |
| 5/4/2005 20:41 | 59.881 | 450 |
| 5/5/2005 17:31 | 59.858 | 450 |
| 5/10/2005 10:42 | 59.888 | 400 |
| 5/18/2005 21:58 | 59.883 | 480 - 3 unit train |
| 5/21/2005 13:27 | 59.851 | 600 - 3 unit train |
| 5/28/2005 23:30 | 59.898 | 330 |
| 5/31/2005 22:28 | 59.815 | 630+ 170 - 2 resources |

Deployed Responsive  (32) (Reported Above)

| 5/1/05 20:21:50 | 5/11/05 15:15:04 | 5/21/05 6:10:22 | 5/26/05 2:03:08 |
| --- | --- | --- | --- |
| 5/2/05 11:33:16 | 5/12/05 6:09:04 | 5/21/05 13:27:28 | 5/26/05 3:33:04 |
| 5/4/05 20:41:20 | 5/12/05 21:58:36 | 5/22/05 6:11:48 | 5/26/05 6:06:38 |
| 5/5/05 17:31:16 | 5/13/05 0:28:28 | 5/22/05 15:05:58 | 5/27/05 22:17:18 |
| 5/6/05 15:53:50 | 5/13/05 10:09:42 | 5/23/05 0:29:20 | 5/28/05 10:14:10 |
| 5/9/05 5:05:44 | 5/14/05 12:49:46 | 5/24/05 6:08:04 | 5/28/05 23:29:52 |
| 5/10/05 10:42:08 | 5/18/05 21:58:08 | 5/24/05 23:31:34 | 5/29/05 2:16:56 |
| 5/10/05 20:26:50 | 5/20/05 6:08:46 | 5/26/05 0:16:10 | 5/31/05 22:28:14 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | May 04 | April 05 | May 05 |
| --- | --- | --- | --- |
| DFW | 133 | 33 | 35 |
| E RIO | 68 | 40 | 55 |
| W RIO | 31 | 29 | 33 |
| Laredo | 57 | 37 | 71 |
| Bryan Area | 0 | 2 | 24 |
| Corpus | 31 | 30 | 31 |
| Abilene | 24 | 0 | 0 |
| San Angelo | 28 | 0 | 0 |
| Western | 17 | 2 | 5 |
| Houston | 0 | 2 | 28 |
| San Antonio | 0 | 1 | 0 |
|  | 389 | 176 | 282 |

| OOME / Congestion Management Activity Contingency | Overloaded Element | # Occur |
| --- | --- | --- |
| Gibbons Creek - Bryan - Greens Prairie 138kV | TAM - Dansby 138kV | 28 |
| Austrop - Sandow 345kV | Austrop 345/138kV Auto #1 | 15 |
| Lytton Spring - Zorn & Austrop - Zorn 345kV | Luling - Zorn 138kV | 14 |
| Salem 345/138kV Auto | Fayette Plant - Fayetteville 345kV | 12 |
| Hill Country - Marion & STP 345kV | Marion - Skyline 345kV | 9 |
| Dilley Switch - San Miguel 138kV | Derby - Pearsall 69kV | 6 |
| LaPalma 345/138kV auto | Rio Hondo - LaPalma 138kV | 5 |
| Vernon - Lake Pauline 138kV | Chilicothe - Vernon 69kV | 4 |
| Lytton Springs-Zorn &Zorn-Austrop 345 | Canyon - Rohr 138kV | 3 |
| Centerville Road - Forney Switch 345kV | Duck Creek Tap - Forney Switch | 3 |
| STP - Skyline 345kV | Blessing - Lolita 138kV | 3 |
| Venus Switch - Everman Switch 345kV | Venus Switch - Webb 345kV | 3 |
| Allen - Renner & Plano Tennyson 345kV | Allen Switch - Plano Alma Road 138kV | 2 |
| Gibbons Creek - Bryan - Greens Prairie 138kV | Hearn - Hearn Sws 69 kV | 2 |
| Gibbons Creek - Twin Oaks 345kV | Jewett - Watson Chapel 138kV | 2 |
| Graham - Benbrook & Graham - Parker Switch 345kV | Stephenville TU - Lingleville Tap 138kV | 2 |
| Lewisville Sw 345/138kV Auto | Carrollton NW-Lake Point 138kV | 2 |
| Live Oak CSW T1 138/69 kV auto | Friend Ranch-Ozona 69kV | 2 |
| North Denton 138/69kV #1 Auto | North Denton 138/69kV #2 | 2 |
| Odessa - Moss 345kV | Odessa EHV-Huntsman 138kV | 2 |
| Rio Hondo - LaPalma 345kV | Rio Hondo - LaPalma 138kV | 2 |
| Zorn - Hays Energy 345kV | Zorn 345/138kV Auto #2 | 2 |
| Allen Switch - Royse Switch & Monticello 345kV | Tricorner - Watermill 345kV | 1 |
| Asherton - West Batesville 138kV | Derby - Pearsall 69kV | 1 |
| Big Brown - Richland Chamber 345kV | Tricorner - Watermill 345kV | 1 |
| Coleto Creek - Kenedy SW 138kV | Leon Creek to Pleasanton 138kV | 1 |
| Comanche Peak - Comanche Switch 345kV | Granbury - Wright 69kV | 1 |
| Dilley Switch - North Laredo 138kV | Asherton - North Laredo 138kV | 1 |
| Ennis Sw - DeSoto Sw 138kV | MG Iindustries-Sterret 138 | 1 |
| Ferguson - Wirtz 138kV | Ferguson-Wirtz 138kV | 1 |
| Friend Ranch - Big Lake 138kV | Friend Ranch to Crockett Heights 69kV | 1 |
| Frontera - McAllen 138kV | Frontera to Sharyland 138kV | 1 |
| Frontera - South McAllen 138kV | Frontera - North McAllen 138kV | 1 |
| Heights Sub - Freeway Park 138kV | Heights Sub - PH Robinson 138kV | 1 |
| Laredo Plant 138/69kV T1 | Laredo 138/69kV A2 auto | 1 |
| Lon Hill - Koch 138kV | McKenzie - Westside 138kV | 1 |
| Lytton Spring - Zorn & Austrop - Zorn 345kV | Canyon-Camp Gary 69 kV | 1 |
| Lytton Spring-Zorn-Austrop 345kV | Lockhart 138/69 kV Auto | 1 |
| Marion - Hill Country & Skyline 345kV | Cibolo - McQueeney 138kV | 1 |
| Marion - Zorn - Clear Springs 345kV | Zorn - Sequin 138kV | 1 |
| Martin Lake - Mt Enterprise 345kV | Nacogdoches South Tap-Lufkin 138kV | 1 |
| North Edinburg - North McAllen 138kV | Pharr - Pharr MVEC 138kV | 1 |
| North Edinburg - Rio Hondo 345kV | South McCallen - Las Milpas | 1 |
| North McAllen - North Edinburg 138kV | Pharr MVEC - Pharr 138kV | 1 |
| Odessa EHV - Moss Switch 138kV | Rexal - General Tire 138kV | 1 |
| Odessa-Moss 345kV | Odessa EHV-General Tire Sw 138 | 1 |
| Oran Tu - RW Miller 138kV | Stephenville TU - Lingleville Tap 138kV | 1 |
| Rio Hondo - LaPalma 345kV | LaPalma 345/138kV Auto | 1 |
| Sandow SES - Temple Sws 345kV | Watson Chapel to Robertson 138kV | 1 |
| Skyline - Marion & STP 345kV | Hill Country - Marion 345kV | 1 |
| Sommerset - Lytle 138kV | Leon Creek - Pleasanton 138kV | 1 |
| Watermill-Trinidad 345kV | Tricorner-Water Mill 345kV | 1 |
| Zorn - Hays Energy 345kV | Zorn Auto 1 | 1 |

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

# New RAP/SPS

The Summer 2005 summary of approved RAP is located at

http://www.ercot.com/tmaps/ListMaps.cfm?GroupID=60

New Procedures/ Forms/Operations Bulletins

5/3	MOB 26	Clarification of Replacement Reserve Service (RPRS) Bid Requirements

5/17	POB 168	Mitigation Plans

5/17	POB 167	Procedure for canceling OOME

# Security Alert Stage/ Threatcon/ Related issues

None/Yellow

Major system voltage problems, Blackout/Load Shed incidences

None

Update on new generation

5/4	70 MW unit in the Coast Zone commercially available.

Communication

5/20	Held 13:30 interval until the 13:45 interval.  ERCOT lost frequency control from 13:28 – 13:57

5/20	Held 16:45 deployments and resumed with 17:30 deployments.  Hour – Ahead study failed to solve.

5/23	Portal inoperable.

Major Computer Problems, Enhancements & Fixes

5/18	AGC software enhancement installed to correct occurrences of irregular regulation deployments.

ERCOT peak (Unofficial)

5/22		17:00	52150

OCN, Advisory, Alert, Emergency Notice and Major Events

| Alerts, OCNs, and Advisories |  |  |  |
| --- | --- | --- | --- |
| 03-May-05 | 10:30-20:35 | Transmission Alert | Sandow 345/138 KV Tr loading |
| 09-May-05 | 14:54 - 18:00 | Transmission Alert | Post Contingency loading of Denton Avenue - Handley 69 kV Tr and Saginaw 138/69 kV Tr |
| 12-May-05 | 15:03 - 23:00 | Transmission Alert | Loss of Gibbons - East/Bryan - Greens Prairie loads Dansby - Texas A&M |
| 13-May-05 | 20:00-24:00 | OCN | Severe weather in the North West Texas area. |
| 13-May-05 | 12:00-21:05 | Transmission Alert | Post contingency loading of Pearsall - Derby 69 Kv, Dilley 138/69 Tr, Derby Sub - Dilley Sub 69 Kv, Dilley Sub - Dilley Switch 69 Kv, Asherton - North Laredo 138 Kv. Laredo 3 forced out |
| 14-May-05 | 5:30 - 15:00 | Alert | Alert issued for capacity insufficiency for hours 1600 – 2100 |
| 14-May-05 | 03:30 - 5:30 | OCN | OCN issued for capacity insufficiency for hours 1600 – 1900 |
| 14-May-05 | 03:12 - 5:30 | OCN | OCN issued for Central and North Texas for severe weather |
| 15-May-05 | 9:15 - 11:00 | OCN | OCN - Possible Capacity shortage for hours 1700 – 2000 |
| 17-May-05 | 13:00 - 17:00 | Alert | Real-time Ancillary Service shortage. Market opened to procure RRS and URS services |
| 17-May-05 | 14:01 - 16:25 | Transmission Alert | Post contingency loading of Johnson Switch - Montague 69 Kv. |
| 17-May-05 | 11:21 - 13:00 | Transmission Alert | Post contingency loading of Chilicothe - Vernon 69 Kv |
| 17-May-05 | 11:25 - 14:01 | Transmission Alert | Post contingency loading of Seguin 138/69 Kv Tr |
| 18-May-05 | 11:57 - 17:20 | Transmission Alert | Loss of Denton Tr 1 loads North Denton 138/69 Kv Tr and North Sanger - Spring 138 Kv. |
| 20-May-05 | 13:43-14:40 | Advisory | Loss of EMS controls |
| 20-May-05 | 08:01-09:48 | Alert | Capacity Insufficiency for intervals 16:00 -18:00 |
| 20-May-05 | 11:20-16:00 | OCN | Capacity Insufficiency for intervals 16:00 -18:00 |
| 20-May-05 | 4:00-09:48 | OCN | Capacity Insufficiency for intervals 16:00 -18:00 |
| 21-May-05 | 13:50 - 21:00 | Transmission Alert | Loss of Gibbons - East/Bryan - Greens Prairie loads Dansby - Texas A&M |
| 22-May-05 | 15:45-22:00 | Transmission Alert | Loss of Dilley - San Miguel loads Derby - Pearsall |
| 23-May-05 | 10:00 - 13:30 | Alert | Capacity Insufficiency for intervals 16:00 -18:00 |
| 23-May-05 | 04:22 - 13:30 | OCN | Capacity Insufficiency for intervals 16:00 -19:00 |
| 24-May-05 | 08:30 - 12:30 | OCN | Capacity Insufficiency for intervals 16:00 -18:00 |
| 31-May-05 | 15:30 - 22:37 | Transmission Alert | Transmission Alert - Actual overload on Bates - Palmhurst 69 Kv |
| 31-May-05 | 16:30 - 18:10 | Transmission Alert | Loss of Euless - Liggett 138kv overloads Roanoke - McPherson 138 Kv |
| 31-May-05 | 11:00 - 12:15 | Transmission Alert | Loss of Euless - Liggett Switch 138kv overloads Saginaw - Haltom 138 Kv |
| 31-May-05 | 15:10 - 19:30 | Transmission Alert | Loss of Laredo Plant 138/69kv Tr 1 loads Laredo 138/69 Tr 2 |

5/8	Thunderstorms in the Coast Zone interrupted service to 100,000 + customers.

5/14 	00:30	Severe weather in West Texas forced out five 69 kV lines and two 138 kV lines.

5/20	Venus SPS activation(s)

5/29 -5/30	Thunderstorms in the Coast Zone interrupted service to 100,000 + customers.

5/31	22:30	Severe weather in West Texas forced out 2 345 kV busses and multiple 345 kV lines.

Figure 1

00:45-00:55 Calculated SCE ~ 800 lower then telemetered and Up Regulation becomes depleted.  The two values diverge at about 00:12.  At 01:05 the large SCE is corrected.  700 MW total VDI issued for Interval 01:15 - 01:30 to compensate (down instruction).

IE 1: 	 PROCURED 1150 Down Regulation and 560 MW Up Regulation (ran out at 00:33)

IE 2-5:  PROCURED 625  Down Regulation and 415 MW Up Regulation (ran out 01:05,01:26)

Differences between actual tie flow and scheduled were often of similar magnitude of available Regulation.

700 MW SCE at 00:40 contributed to high frequency.  Much of the poor control can be attributed to under compensating and then over compensating for curtailed tags.  Curtailed imports or exports are not visible in a QSE SCE and must be off set in the balancing energy procured.

Major contributing factor to poor performance was the lack of compensation for curtailments in the offset calculation.

- Temperatures in ERCOT rise earlier in the season than most of the rest of the Eastern Interconnect which results in a high import during this season.

- Overscheduling imports in the MOI indicates that either the interface was oversold, or the QSE scheduling the import is not securing reservations prior to submitting schedules in the ERCOT MOI.

The amount of Regulation procured for May between 01:00 – 05:00 is relatively small.

Large fluctuations in SCE also contributed to poor control. (+700 at 00:40 and -500 at 01:05)