| OGRR Number | 169 | OGRR Title | Reporting of Reserve Capability Under Severe Gas Curtailments |
| --- | --- | --- | --- |
| ###### Date |  | 6/20/05 |  |
| ## Submitter’s Information |  |  |  |
| Name |  | Steve Knapp, on behalf of OGRTF |  |
| E-mail Address |  | steve.knapp@constellation.com |  |
| Company |  | Constellation Energy |  |
| Company Address |  | 111 Market Place, Ste 500, Baltimore, MD 21202 |  |
| Phone Number |  | 410-468-3606 |  |
| Fax Number |  |  |  |

Comments

OGRTF submits the following revised language for clarification purposes.

Proposed Operating Guide Language Revision

#### 3.1.4.1	PGC Data Reporting

The PGC’s reporting QSE shall provide the following information to ERCOT Control Area Authority at the times specified:

| TIME | INFORMATION |
| --- | --- |
| Every 10 seconds | - Generation net MW output - Generation net MVAR - Status of switching devices in switchyard - Generating unit breaker status - Generating unit High Operating Limit - Generating unit Low Operating Limit |
| Daily | - Planned unit status, - Planned unit capability (both hourly and daily), - Fuel limitations. The reporting Entity will promptly report this condition to ERCOT Control Area Authority |
| Annually | - Seasonal capability where applicable - Data for Winter Preparedness Report Form (Section 6) - Planned maintenance schedules. This information shall be updated when it changes. |

Each Generator at a generation facility shall have an automatic speed governor in service while the Generator is on line.  Testing and regulation performance of the speed governor shall be in accordance with Operating Guide Section 3.  The Generator is required to notify the ERCOT Control Area Authority, through its QSE if the operation of speed governors is impaired.

Each generation facility providing an Ancillary Service shall provide output consistent with the requirements of that Ancillary Service and ERCOT instructions.

In the event of an ERCOT declared emergency, ERCOT may require the QSE to notify the generation facility through the reporting Entity and require it to increase or decrease generation or change voltage and reactive requirements in accordance with the Protocols.  The generation facility shall use its best efforts in meeting these required output levels in order that the ERCOT System can maintain safe and reliable operation.

It is the responsibility of all Generators to carry an operational share of reactive support to insure adequate and safe Voltage Profiles are maintained in all areas of ERCOT.  To accomplish this, the following requirements shall apply to each generation facility.

- Each generation facility shall have Automatic Voltage Regulators and power system stabilizers in service as defined in Section 3.1.4.5, Automatic Voltage Regulators And Power System Stabilizers, below.

- The generation facility shall be designed and operated consistent with its obligations to supply Voltage Ancillary Service as required in the ERCOT Protocols and ERCOT Control Area Authority Procedures.

- ERCOT has the right and obligation to Dispatch the reactive output (VARS) of each generation facility within its design capability to maintain adequate transmission voltage in ERCOT.

- ERCOT and the TSP shall be notified of any equipment changes that affect the reactive capability of an operating generating unit no less than 60 days prior to implementation of the changes, and any such changes that decrease the reactive capability of the generating unit below the required level must be approved by ERCOT prior to implementation.

- High reactive loading or reactive oscillations on generation units should be communicated to the QSE, the Transmission Operator, and ERCOT as soon as practicable.

- The tripping off line of a generating unit due to voltage or reactive problems should be reported to ERCOT, the Transmission Operator, and the QSE as soon as practicable.

Reference:  Protocols, Section 6.10.2, General Capacity Testing Requirements

6.10.2	General Capacity Testing Requirements

QSEs shall provide ERCOT a list identifying each Generation Resource unit that is expected to operate more than one hundred sixty eight (168) hours in a Season as a provider of energy and/or Ancillary Services.  ERCOT shall evaluate, during each Season of expected operation, the Net Dependable Capability of each unit expected to operate more than one hundred sixty eight (168) hours during that Season, except for any Generation Resources used solely for energy services and whose capacity is less than ten (10) MW.  Prior to the beginning of each Season, QSEs shall identify the Generation Resources to be tested during the Season and the specific week of the test if known.  This schedule may be modified by the QSE (including retests) during the Season.  QSEs not identifying a specific week for a Generation Resource unit test must test the unit within the first one hundred sixty eight (168) hours of run time during the Season or operate with a Net Dependable Capability equal to the highest integrated hourly MWh output demonstrated during the first one hundred sixty eight (168) hours of run time.  QSEs do not have to bring units On-line or shut down solely for the purpose of the seasonal verification.  Any unit for which the QSE desires qualification to provide Ancillary Services shall have its Net Dependable Capability verified prior to providing services using the Generation Resource unit even if it fits the less than one hundred sixty eight (168) hour or small capacity exception.  The capability of hydro units operating in the synchronous condenser fast response mode to provide hydro Responsive Reserve shall be evaluated by Season.

Load acting as a Resource to provide Ancillary Services shall have its telemetry attributes verified by ERCOT annually.  In addition, once every two (2) years, any LaaR providing Responsive Reserve Service shall test the under frequency relay or the output from the solid-state switch, whichever applies, for correct operation.  However, if the Load’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and/or the biennial relay testing requirement.

6.2.7	Unit Alternative Fuel Capability Data for Winter Preparedness Report

General Information

Unit Code (16 character):			Location (County):

Unit Name:

Generator’s QSE:				Resource Entity:

Fuel information

Primary Fuel:		Alternative Fuel:

MW Capability:				MW Capability:

Is the Resource capable of Starting up on Alternative Fuel? ______

Is the Resource capable of going to 100% Alternative Fuel once started? ______

If the Resource must run on a blend of Primary Fuel & Alternative Fuel, please specify the maximum % Alternative Fuel:  ______

Please specify the number of hours required to transition from 100% Primary Fuel to maximum % Alternative Fuel:  _____

Current Capability

Number of hours at max capability on Alternative Fuel:

Estimated time required to replenish the supply and by what source (i.e. pipeline, truck, etc...):

Firm Primary Fuel Delivery contract to Burner Tip

Hours per day at Max Capability: ______

Max daily Sustainable rate in MW: _________

Is the contract in effect for December 1st through March 1st? __

if the answer is No, please specify the dates for which it is in effect_______

Firm Gas purchase agreement with corresponding firm gas transportation agreement

Hours per day at Max Capability ______

Max daily Sustainable rate in MW _________

Is the contract in effect for December 1st through March 1st? __

if the answer is No, please specify the dates for which it is in effect_______

Expected Capability on December 1st

Number of hours at max capability on Alternative Fuel:

Estimated time required to replenish the supply and by what source (i.e. pipeline, truck, etc...)

Firm Primary Fuel Delivery contract to Burner Tip

Hours per day at Max Capability ______

Max daily Sustainable rate in MW _________

Is the contract in effect for December 1st through March 1st? __

if the answer is No, please specify the dates for which it is in effect_______

Firm Gas purchase agreement with corresponding firm gas transportation agreement

Hours per day at Max Capability ______

Max daily Sustainable rate in MW _________

Is the contract in effect for December 1st through March 1st ? __

if the answer is No, please specify the dates for which it is in effect_______

Limiting Factors:

Please estimate Resource capability under the following scenarios:

|  | Max MW Capability | No. Hrs per Day @ Max | Max daily MW Sustainable | No. Days |
| --- | --- | --- | --- | --- |
| 50% interruptible gas curtailment |  |  |  |  |
| 100% interruptible gas curtailment |  |  |  |  |
| 100% interruptible gas curtailment and 50% firm gas curtailment |  |  |  |  |

Limiting Factors:

Please specify dates of gas curtailments and duration of curtailment during the previous Winter Season

______________________________________________________________

Was the curtailment supply related, contract related, other?

_______________________________________________________________

Submittal

Resource Entity Representative:

QSE Representative:

Date submitted to ERCOT Control Area Authority Rep.: