## Slide 1: Treatment of Generating Unit Contingencies in Operations and Planning Potential Need for Reliability Criteria Clarification Presentation to ROS June 16, 2004

## Slide 2: Operating Guide – Section 2 Operation Criteria
2.2.2 Security Criteria
.
d. … A credible single contingency is defined as the Forced Outage of two generating units in the ERCOT System within a short period of time, or the Forced Outage of any single transmission element (such as a circuit or transformer).

## Slide 3: Operating Guides – Section 5-Planning Criteria
5.1.4 Transmission Reliability Testing
(2) With any single generating unit unavailable, and with any other generation preemptively redispatched, the contingency loss of a single transmission element …

## Slide 4: Why Discuss Now?
Shutdown of generation in urban areas makes voltage collapse a greater risk then it has been historically
The consequence of a voltage collapse in an urban area is much higher then the historic thermal overload consequence; and the required post-contingency speed of diagnosis/response is MUCH faster then resolution of thermal problems.

## Slide 5: Why Discuss Now?
In this slide % outages = # Train Outages/# CC Trains in ERCOT

## Slide 6: Issues
Inconsistency between security operations criteria and planning criteria
Treatment of Combined Cycle plants
  The loss of a steam turbine can make the CT(s) unavailable
    No bypass for the steam
    Single point of failure for both the Steam and CT
  Modeling of the loads netted with CC generation
  Because private networks are not modeled, ERCOT may not adequately detect local load increase or local voltage collapse resulting from a unit trip.

## Slide 7: Recommendation
Changes to Operating Guides:
SECTION 2: Combined Cycle trains modeled as a single contingency
SECTION 5:
Analyze Double Unit outages as well as single unit/single circuit.

## Slide 8: QUESTIONS/DISCUSSION