## Slide 1: SPS policy – Information Presentation Presentation to ROS June 16, 2004

## Slide 2: Definition
Special Protection Scheme (SPS): Section 2.1 of the ERCOT Protocols defines a Special Protection Scheme as, “A protective relay system specially designed to detect abnormal system conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable system performance.” Section 7.2.2.13 of the ERCOT Operating Guides expands upon this definition, stating that, “SPS actions include among others, changes in demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable facility loadings.”

## Slide 3: Approval
SPSs
Special Protection Schemes must meet several requirements before they can be considered for approval. An SPS must:
Be coordinated and approved by all affected parties.
be used in a limited way only for the time required to construct replacement transmission facilities, or replacement transmission facilities have been determined by ERCOT to be unnecessary ( for example, due to excessive cost, inability to construct, or agreement by all parties, etc)
comply with all applicable ERCOT and NERC requirements
be incorporated into the calculations performed by ERCOT where applicable

## Slide 4: Approval
Furthermore, an SPS must:
Be fully automatic.
Not operate except as necessary (see SPS Misoperation)
Consider the possible interactions of multiple SPS installations.
Provide a methodology and medium for ERCOT System Operations to monitor the conditions that would actuate the SPS.
Be approved by ERCOT staff prior to any modification, or after it has been in service for more than five years, or when system conditions have changed; invalidating the original assessment.
  Section 8.8.2 of the ERCOT Protocols states that TOs, “…shall coordinate with ERCOT the following types of work for any addition, replacement or modification to the ERCOT Transmission Grid…”

## Slide 5: Approval
The decision making authority for all SPS approval is ERCOT Operations, which includes System Operations and Transmission Services. There are two time periods for SPS approval: Normal, and Urgent. The Market Participant proposing an SPS has the option of requesting a Normal or Urgent timeline for review. However, the party requesting an Urgent timeline shall provide sufficient justification for the Urgent request (e.g. frequent occurrence of congestion in daily operations) at the time it submits its proposal. ERCOT Transmission Services will determine within two (2) days of receipt if the Urgent request is justified. Normal and Urgent timelines are described as follows:

## Slide 6: Normal Approval
Normal Timeline Review for SPS
The Market Participant who is proposing an SPS will submit the proposal to the lead Transmission Services engineer at ERCOT for the corresponding Regional Planning Group (RGP).
Within two days of receipt, the RPG lead planning engineer will initiate a 30-day review period by ERCOT Transmission Services, ERCOT System Operations, and the associated TO.
Concurrent to the 30-day review period described above, the RPG lead planning engineer will forward the proposal to the appropriate RPG and Operations Review Group (ORG) distribution list. RPG and ORG members will then have 21 days to submit comments on the proposal to ERCOT with copies to the RPG and ORG distribution list. This 21-day comment period will run concurrent with the first 30-days of the review period, leaving nine (9) days for ERCOT to consider comments received prior to issuing a preliminary decision on the proposal.

## Slide 7: Normal Approval
At the end of the 30-day review period, ERCOT Operations will issue a preliminary decision on the proposal to the appropriate RPG and ORG distribution lists.
Market Participants will have 7 days after the filing of ERCOT’s preliminary decision to file any comments regarding that decision to the appropriate RPG and ORG distribution lists.
ERCOT will consider any additional Market Participant comments received and issue a final decision within 10 days of the filing of its preliminary decision. The final decision will be sent to the appropriate RPG and ORG distribution lists.
For an SPS that is approved, the associated TOs will develop and submit to ERCOT an exit strategy on a schedule to be determined by ERCOT. ERCOT, with any needed assistance from the relevant RPG(s) will then assign a status to the SPS, either Temporary or Permanent.
  For a Permanent SPS, the transmission facility exit strategy implementation will be deferred indefinitely until and unless the assigned status is changed by ERCOT.
  For a Temporary SPS, the associated TOs will include the exit strategy in its transmission plan, and will be expected to pursue necessary approvals and construction activity on a schedule consistent with other facilities of comparable necessity in its transmission plan.

## Slide 8: Urgent Approval
The Market Participant who is proposing an SPS for Urgent review will submit the proposal to the lead Transmission Services engineer at ERCOT for the corresponding Regional Planning Group (RGP) and to ERCOT System Operations, along with all supporting information necessary.
ERCOT System Operations may tentatively approve the proposed SPS on an exception basis pending full review. The tentative approval will be treated as ERCOT approval until 9 months after the final ERCOT review is complete.
ERCOT Transmission Services will review the proposed SPS to confirm reliable operation.

## Slide 9: Urgent Approval
ERCOT Transmission Services will then forward successful initial review to appropriate ERCOT Task Forces as deemed necessary. Task Force questions and comments are sent back to ERCOT Transmission Services and addressed. Work with the owner may be necessary to address all issues.
Upon resolution of issues identified in the reviews, the Director of ERCOT Operations, with concurrence of ERCOT Transmission Services and ERCOT System Operations, provides the 5 year approval for the SPS and informs the SPS owner. TAC and subcommittees are informed at their next meeting. ERCOT Transmission Services puts the review documentation on file.

## Slide 10: ERCOT Process
Update SPS manual in Operations
Post SPS to ERCOT secured web site

## Slide 11: Mis-operation
SPS Misoperation is not explicitly defined in the ERCOT Protocols or Operating Guides, but is described as the operation of an SPS when the conditions of the SPS have not been met, or the lack of operation of an SPS when the conditions have been met. The ERCOT Operating Guides section 7.2.3.3 does list several events that could describe an SPS misoperation. These events are listed below:
Failure to Operate – Any failure of an SPS to perform its intended function within the designated time when system conditions intended to rigger the SPS occur.
Failure to Arm – Any failure of a SPS to automatically arm itself for system conditions that are intended to result in the SPS being automatically armed.
Unnecessary Operation – Any operation of an SPS that occurs without the occurrence of the intended system trigger condition(s).
Unnecessary Arming – Any automatic arming of a SPS that occurs without the occurrence of the intended arming system condition(s).
Failure to Reset – Any failure of a SPS to automatically reset following a return of normal system conditions if that is the design intent.

## Slide 12: Mis-operation
When an SPS operates, the TO shall file a report with ERCOT per section 7.2.2 (15) of the ERCOT Operating Guides. After reviewing the report, ERCOT System Operations will make a determination as to whether or not the SPS had misoperated. Executing this process is the responsibility of the Engineer Supervising the Operations Support Group. ERCOT Operations shall make this determination using the process outlined below:
ERCOT System Operations and Transmission Services shall independently review the report filed by the TO.
ERCOT System Operations and Transmission Services shall meet and discuss the results of their review within fifteen (15) working days of the event. Any remaining questions or comments remaining shall be sent to the TO.

## Slide 13: Mis-operation
ERCOT System Operations and Transmission Services shall review the replies from the TO, if any, and prepare a technical opinion as to whether or not the SPS has misoperated within thirty (30) working days of the event.
The technical opinion shall then be sent to the Director of System Operations and the Director of Transmission Services for official determination of correct operation, which will then be sent out to the TO and to the Reliability and Operating Subcommittee.
Should an SPS misoperate 2 times or more for the same reason within the 5 year period of the SPS, ERCOT may request that the SPS be disabled until further review of the SPS and its misoperations can be made.

## Slide 14: Mis-operation
If it is determined that the SPS had misoperated, a request will be made to the TO requesting an outline of steps to be made to ensure that this same misoperation will not happen in the future.

## Slide 15: QUESTIONS/DISCUSSION