## Slide 1: NonSpin Deployment 5/11/2005 Presentation to ROS June 16, 2004

## Slide 2: Logs
Deployed NSRS for interval ending 16:00 through hour ending 18:00. Insufficiency of Balancing Energy due to 2% remaining for 16:00 interval, 30% for 16:15, 4% for 16:30, 4% for 16:35, and 3% for 17:00

## Slide 3: What the Operator Saw Hour Ahead Study
 |  |  |  | BES Cleared |  |  | BES procured |  |  | UBES remaining | 
Date/Interval |  | Gen Sched |  | UBES | DBES |  | BUL | LAAR |  | MW | %
11-May-05 | 16:15 |  |  |  |  |  |  |  |  |  | 2
11-May-05 | 16:30 |  |  |  |  |  |  |  |  |  | 30
11-May-05 | 16:45 |  |  |  |  |  |  |  |  |  | 4
11-May-05 | 17:00 |  |  |  |  |  |  |  |  |  | 3

## Slide 4: ERCOT procedures on NSRS Deployment
VERIFY UBES Remaining. IF >5% of available UBES remains undeployed, no further action is necessary. IF <5% remaining proceed.
DETERMINE if NSRS deployment is necessary for balancing support.DETERMINE if load forecast value in studies accurately reflects trending of real time load for the same interval(s). If Load forecast is inaccurate (medium term), NOTIFY the Frequency Desk and the Shift Supervisor. Log actions and stop. Otherwise, proceed.
IF NSRS is scheduled and available, deploy (see Appendix 4: Deploy NSRS) as needed to resolve UBES deficiency. IF NSRS is unscheduled or unavailable, notify the Frequency Desk and Shift Supervisor of need for VDI or OOM. (MW value and time).

## Slide 5: QUESTIONS/DISCUSSION