## ERCOT Operations Report

## ROS & OWG

## June 2005

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 6/2/2005 5:59 | 60.116 | 28823 | 388 | 457 | 2600 (775) |
| 6/10/2005 1:10 | 60.117 | 34598 | -572 | 3 | -1000 (-790) |
| 6/16/2005 0:15 | 60.104 | 38182 | 147 | 167 | -3090 (-1315) |
| 6/16/2005 19:02 | 59.899 | 54970 | -86 | -22 |  |
| 6/21/2005 2:10 | 60.101 | 30397 | -260 | 140 | -900 (-700) Frequency above 60.1 for 2 seconds. |
| 6/21/2005 22:05 | 60.105 | 43755 | -1097 | 690 | -5500 (-1440) |
| 6/23/2005 4:14 | 60.127 | 30061 | -499 | 117 | VDI issued to reduce generation. HA study ran prior to significant changes in resource plan |
| 6/25/2005 0:06 | 60.106 | 36958 | -43 | 181 | -2280 (-600) |
| 6/27/2005 1:18 | 60.108 | 33412 | -126 | 71 | Non conforming load and significant rate of load change |
| 6/27/2005 15:10 | 59.881 | 53828 | 811 | -191 |  |
| 6/28/2005 20:00 | 60.102 | 51369 | -557 | 810 | -3575(-935) |
| 6/30/2005 10:12 | 59.865 | 45756 | 599 | -606 | 2400 (500) |

| Disturbance Data |  |  |
| --- | --- | --- |
| 6/1/2005 18:48 | 59.880 | 518 MW |
| 6/3/2005 3:01 | 59.859 | 580 MW |
| 6/15/2005 5:22 | 59.846 | 570 MW |
| 6/22/2005 23:34 | 59.812 | 780 |
| 6/26/2005 1:09 | 59.843 | 523 MW. Additional 500 MW run back 00:55 - 01:00 |
| 6/28/2005 10:56 | 59.894 | 600 MW run back |

Deployed Responsive (32) (Reported Above)

| 6/1/05 0:28 | 6/11/05 2:46 | 6/18/05 1:45 | 6/26/05 0:56 |
| --- | --- | --- | --- |
| 6/1/05 18:48 | 6/11/05 7:31 | 6/19/05 20:15 | 6/26/05 1:09 |
| 6/2/05 12:20 | 6/14/05 1:18 | 6/21/05 1:18 | 6/26/05 2:48 |
| 6/3/05 3:01 | 6/14/05 17:32 | 6/22/05 23:34 | 6/27/05 4:45 |
| 6/4/05 0:42 | 6/15/05 5:22 | 6/23/05 0:01 | 6/27/05 4:59 |
| 6/6/05 5:06 | 6/16/05 10:14 | 6/23/05 3:01 | 6/27/05 15:03 |
| 6/7/05 7:05 | 6/16/05 19:02 | 6/24/05 9:04 | 6/28/05 10:56 |
| 6/9/05 7:08 | 6/17/05 23:51 | 6/25/05 23:59 | 6/30/05 10:05 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Jun 04 | May 05 | June 05 |
| --- | --- | --- | --- |
| DFW | 226 | 35 | 84 |
| E RIO | 120 | 55 | 90 |
| W RIO | 60 | 33 | 34 |
| Laredo | 79 | 71 | 90 |
| Bryan Area | 0 | 24 | 32 |
| Corpus | 30 | 31 | 29 |
| Abilene | 29 | 0 | 0 |
| San Angelo | 30 | 0 | 0 |
| Western | 36 | 5 | 24 |
| Houston | 0 | 28 | 15 |
| San Antonio | 2 | 0 | 0 |
|  | 612 | 282 | 398 |

OOME / Congestion Management Activity

| Days of Zonal Congestion |  |
| --- | --- |
| South to Houston | 25 |
| South to North | 8 |
| North to Houston | 7 |
| North to West | 7 |

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overloaded Element | # Occurrences |
| --- | --- | --- |
| Gibbons Creek - Bryan E - Greens Prairie 138kV | TAM - Dansby 138kV | 30 |
| Sandow - Austrop 345kV | Austrop Auto | 19 |
| Odessa - Moss 138kV | Odessa - Huntsman 138kV | 13 |
| Lytton Springs - Zorn - Austrop 345 | San Marcos-Canyon LCRA 138kV | 11 |
| Marion - Zorn & Clear Spring 345kV | Zorn - Seguin 138kV | 9 |
| Lewisville 345kV Auto | Carrollton NW - Lakepoint 138kV | 8 |
| Frontera - South McAllen 138kV | North McAllen - West McAllen 138kV | 7 |
| Hill Country - Marion - STP 345 | Marion - Skyline 345 | 7 |
| Lytton Spring - Zorn & Austrop - Zorn 345kV | Zorn - Luling 138kV | 5 |
| Bates Auto | North Edinburg – Moore Field 69kV | 3 |
| Centerville - Forney 345kV | Lake Hubbard - Duck Creek Tap 138kV | 3 |
| North Edinburg - Rio Hondo 345kV | South McAllen - Las Milpas 138kV | 3 |
| Skyline - Marion & STP 345kV | Marion - Hill Country 345kV | 3 |
| Allen - Renner & Plano Tennyson 345kV | Allen Switch - Plano Parker Road 138kV | 2 |
| Allen Switch - Plano Tennyson & Renner Switch 345kV | Allen Switch - Plano Custer Road 138kV | 2 |
| Buda - Turnersville 138kV | Kendall CTEC - Kendall 138kV | 2 |
| McNeil AEN - Decker Power Plant 138kV | Decker - Sprinkle 138kV | 2 |
| Sargant Rd - Watermill 345kV | Mt Creek - Cedar Hill 138kV | 2 |
| Trinidad - Watermill & Trinidad - Tricorner 345kV | Trinidad Auto | 2 |
| Carroll-n NW - Forney 345kV | Lake Hubbard - Duck Creek Tap 138kV | 1 |
| Collin Auto | Renner - Plano Coit 138kV | 1 |
| Elkton - Tricorner - Martin lake 345kV | Stryker - Cushing 138kV | 1 |
| Elkton - Tricorner - Martin Lake 345kV | Stryker Creek - Troup 138kV | 1 |
| Ennis Switch - Deso- Switch 138kV | Sterrett -Waxahachie Pump 138kV | 1 |
| Ennis Switch - Desoto- Switch 138kV | Sterrett - Ennis Switch 138kV | 1 |
| Euless - Liggett Switch 138kV | Lewisville - Lewisville Switch 138kV | 1 |
| Gibbons Creek - Twin Oak SW 345kV | Jewett - Watson Chapel 138kV | 1 |
| Gibbons Creek - Twin Oaks 345kV | Greens Prairie - Gibbons Creek 138kV | 1 |
| Hill Country - Marion & STP 345kV | Hill Country - Marion 345kV | 1 |
| Jewett - TH Wharton & Tomball 345kV | Waller -Prairie View 138kV | 1 |
| La Palma - Rio Hondo 345kV | La Palma - Rio Hondo 138kV | 1 |
| Lake Pauline 138/69kV Auto | Vernon - Grayback 69kV | 1 |
| La Palma - Rio Hondo 345kV | La Palma - Rio Hondo 138kV | 1 |
| Lon Hill - Nueces Bay 138kV | Lon Hill Auto | 1 |
| Marion - Hill Country & Skyline 345kV | Schertz - Parkway 138kV | 1 |
| Marion - Hill Country & Skyline 345kV | Three Rivers Auto | 1 |
| Marion - Zorn - Clear Spring 345kV | McCarty Rd. - Henne 138kV | 1 |
| N McAllen - W McAllen 138kV | Frontera-S McAllen 138kV | 1 |
| N Edinburg - Bates 138kV | N Edinburg - Moore Field 69kV | 1 |
| Pharr - Pharr MVEC 138kV | N McAllen - W McAllen 138kV | 1 |
| Salem Auto | Fayette -Fayetteville 345kV | 1 |
| Sargent Rd - Watermill 345kV | Cedar Hill Sw Auto | 1 |
| Sonora - Friend Ranch 138kV | Friend Ranch - Ozona 69kV | 1 |
| Stryker Creek - Trinidad 345kV | Stryker Creek - Summerfield Tap 138kV | 1 |
| Trinidad - Stryker & Mt. Enterprise 345kV | Stryker - Dialville 138kV | 1 |
| Uvalde - Hamilton 138kV | Asherton - West Conoco 138kV | 1 |
| West Columbia Main - West Columbia 138kV | West Columbia - Pledger 138kV | 1 |
| West Side CSW - Airline CSW 138kV | Port Aransas - Mustang Island 69kV | 1 |
| Zorn - Hays Energy 345kV | Kendall AT1 Auto | 1 |

# New RAP/SPS

6/17		Austrop SPS

6/29/05	Tyler West – Elkton RAP

New Procedures/ Forms/Operations Bulletins

| 06/30/2005 | POB 190 | Transmission & Security Desk V3R51 - DFW Reactive Reserves. |
| --- | --- | --- |
| 06/30/2005 | POB 189 | Transmission & Security Desk - Remedial Action Plans |
| 06/30/2005 | POB 188 | Transmission & Security Desk - RTCA Congestion Management. |
| 06/30/2005 | POB 187 | Frequency Control Desk - Maintenance Level 2 and 3 Outages |
| 06/30/2005 | POB 186 | Frequency Control Desk - Replace RRS through a Bilateral Trade. |
| 06/30/2005 | POB 185 | Frequency Control Desk - South DC Tie |
| 06/21/2005 | POB 184 | Transmission & Security Desk - Guidelines for Withdrawal of an Outage. |
| 06/21/2005 | POB 183 | Transmission & Security Desk - Manage Forced and Level 1 Maintenance Outages |
| 06/21/2005 | POB 182 | Operating Period Desk - Temporary Change: Automated Offset Calculations. |
| 06/21/2005 | POB 181 | T&S Desk - Temporary Change: Maintenance Level 2 and 3 Outages. |
| 06/16/2005 | POB 180 | Transmission & Security Desk V3R46 - OOME VDI Guidelines |
| 06/16/2005 | POB 179 | T & S Desk V3R45 - RTCA Congestion Management Call Out Procedure |
| 06/16/2005 | POB 178 | Transmission & Security Desk V3R44 - Remedial Action Plans |
| 06/14/2005 | POB 177 | Transmission & Security Desk V3R43 - Mitigation Plans |
| 06/14/2005 | POB 176 | Transmission & Security Desk V3R42 - Verbal Dispatch Instructions |
| 06/14/2005 | POB 175 | Frequency Control Desk V3R27 - Verbal Dispatch Instructions |
| 06/14/2005 | POB 174 | Frequency Control Desk - Use of LAARs to Arrest a Reportable Low Frequency Disturbance |
| 06/06/2005 | POB 173 | Transmission & Security Desk - Zonal (CSC) Congestion Management |
| 06/06/2005 | POB 172 | Shift Supervisor Desk - QSE Transferring to Backup Control Center |
| 06/06/2005 | POB 171 | Transmission & Security Desk - Temporary Change for Western Area Action Plan |
| 06/06/2005 | POB 170 | Day Ahead Desk - Modified Non Spin Procurement Methodology |
| 06/02/2005 | POB 169 | The Transmission Outage Approval Process |

# Security Alert Stage/ Threatcon/ Related issues

None/Yellow

Major system voltage problems, Blackout/Load Shed incidences

None

Update on new generation

18 MW wind resource in the West Zone outside of the McCamey area.

Communication

6/1	Held 01:45 interval.  SPD failed to solve.

6/8	Extended Day ahead market to 15:00.

6/14	12:50 – 13:10	Portal down.

6/23	12:30 RTBM did not clear and the 12:15 interval was held.

Major Computer Problems, Enhancements & Fixes

6/15	09:00	EMS migration of Release 4.

ERCOT peak (Unofficial)

6/30		17:00	58285

| OCN, Advisory, Alert, Emergency Notice |  |  |  |
| --- | --- | --- | --- |
| 2-Jun | 14:50 - 16:30 | Transmission Alert | Loss of Euless - Liggett 138kv loads Lewisville Switch - Lewisville 138kv. |
| 2-Jun | 9:30 - 11:30 | OCN | Capacity insufficiency for HE 1700 - 1800. |
| 4-Jun | 15:11-18:20 | Transmission Alert | Loss of Gibbons Creek - Bryan E - Greens Prairie loads Texas AM-Dansby. |
| 4-Jun | 14:40-23:15 | Transmission Alert | Loss of Allen Switch - Plano Tennyson & Renner loads Allen Switch - Plano Custer. |
| 6-Jun | 12:47-16:00 | Transmission Alert | Loss of Elkton-Tricorner-Martin Lk loads Tyler NE- Tyler E. |
| 7-Jun | 09:59-17:00 | OCN | Capacity insufficency for HE 1600 - 1800. |
| 10-Jun | 16:50 - 20:30 | Transmission Alert | Loss of Lake Pauline Tr. loads Vernon - Grayback. |
| 10-Jun | 16:50 - 20:30 | Transmission Alert | Loss of San Miguel Tr. loads Derby-Pearsall. |
| 10-Jun | 16:50 - 20:30 | Transmission Alert | Ballinger - Paint Rock over post contingency limit. |
| 14-Jun | 13:45-14:45 | Transmission Emergency | Bryan and College Station Area, force outage in area. |
| 14-Jun | 22:00-24:00 | Advisory | Capacity shortage for 6/15. |
| 15-Jun | 08:00 - 16:00 | Alert | Capacity Shortage in Resource Plans for HE 1600 - 1900. |
| 15-Jun | 00:09 | Advisory | Capacity shortage for 06/15, HE 1600 - 1800. |
| 16-Jun | 00:25 - 20:00 | Alert | Capacity Shortage in Resource Plans for hours 1600 - 1900. |
| 20-Jun | 14:44 - 20:15 | Transmission Alert | Loss of San Miguel Tr. loads Derby-Pearsall. |
| 24-Jun | 10:40 - 11:20 | Transmission Alert | Loss of Moore - Hondo Creek loads Downie 138/69 Tr. |
| 25-Jun | 03:44 - 0600 | OCN | Capacity shortage for HE 17:00 -19:00. |
| 25-Jun | 0600 - 12:00 | Alert | Capacity Shortage in Resource Plans for HE 1700 - 1900. |
| 27-Jun | 01:02-18:30 | OCN | Capacity insufficiency for HE 1400 - 1800. |
| 27-Jun | 14:06-21:00 | Transmission Alert | Loss of San Miguel Tr. loads Derby-Pearsall. |
| 27-Jun | 14:13-21:00 | Transmission Alert | Loss of Bates Auto loads N Edinburg - Moore Field. |
| 27-Jun | 18:21-23:02 | Transmission Alert | Loss of Gibbons Creek -Twin Oak loads Gibbons Creek - Bryan Greens Prairie. |
| 28-Jun | 15:56 - 20:30 | Transmission Alert | Loss of Tyler West - Elkton loads Tyler West Tr. |
| 28-Jun | 11:30 - 13:20 | Transmission Alert | Loss of North Edinburg - Bates loads North Edinburg - Moore Field. |
| 28-Jun | 15:54 - 22:00 | Transmission Alert | Loss of Gibbons Creek -Twin Oak loads Gibbons Creek - Bryan Greens Prairie. |
| 28-Jun | 13:17 - 20:30 | Transmission Alert | Loss of San Miguel Tr loads Derby-Pearsall. |
| 28-Jun | 02:05 - 17:15 | OCN | Capacity shortage for HE 1600 - 1800. |
| 28-Jun | 08:40 - 17:15 | OCN | Capacity shortage for HE 1600 -1900. |
| 29-Jun | 13:16 - 22:30 | Transmission Alert | Loss of Gibbons Creek -Twin Oak loads Gibbons Creek - Bryan Greens Prairie. |
| 29-Jun | 15:07 - 22:30 | Transmission Alert | Loss of Forest Hill 138/69 loads Handley - Duval. |
| 29-Jun | 13:31 - 22:30 | Transmission Alert | Loss of San Miguel Tr loads Derby-Pearsall. |
| 30-Jun | 15:13 - 21:30 | Transmission Alert | Loss of Lewisville 345/138 Tr loads Carrollton Northwest - Lakepoint. |
| 30-Jun | 14:51 - 21:30 | Transmission Alert | Loss of Forest Hill 138/69 loads Handley - Duval. |
| 30-Jun | 14:36 - 22:30 | Transmission Alert | Loss of San Miguel Tr loads Derby-Pearsall. |

Major Events

6/22 16:36	 Oklaunion to Fisher Road Switch 345 kV tripped, also removing Fisher Road – Bowman 345 kV and the 345/138 kV transformer at Fisher Road (there are no breakers on the Fisher Road 345 kV bus).  Additionally, the 345/138 kV transformer #2 At Oklaunion tripped on the low side for an unknown reason.  No element overloads were observed, but Real-Time contingency analysis (RTCA) failed to solve for approximately 25 minutes.

The simulated contingency loss of the Oklaunion unit caused the RTCA to produce no results.  Running contingency analysis in a study mode also produced no results.  This contingency was disabled and RTCA was restored at approximately 17:26 and ran normally for about 30 minutes. After 18:03, RTCA was giving indication that it was running and solving, but the display of results was not changing.  This was not initially identified and was not resolved until 20:40.

The worst observed contingency was the loss of the single 345 kV Bowman Switch to Jacksboro, which caused low voltage at multiple northwestern 138 and 69 kV busses and thermal loading of the order of 180% post contingency on the 138 kV system around the Graham station, including Graham to Rice Switch, Rice to Markley, Markley to Windthorst Switch.  Bowman Switch to Fisher Road Switch and the Fisher Road Switch 345/138 kV transformer were returned to service by 16:56.  ERCOT requested TXU ED to open the 345/138 kV transformer at Graham and requested Oklaunion to reduce generation by ~100 MW.  The North DC Tie was now isolated and the only export path was the remaining 345/138 kV transformer 1 at Oklaunion.  At 16:42, the North DC Tie was opened, carrying 100 MW.  TXU ED opened the 345 kV transformer at Graham under the direction of ERCOT.  Low voltages were observed by ERCOT and TXU ED on the 138 kV system around Graham.  The transformer was opened at 16:53 and reclosed by TXU ED at 16:57.  Prior to the switching, the Stephenville – Lingleville 138 kV line 1800_C pre contingency loading was ~72 MVA.  The loading increased to ~100 MVA for approximately 4 minutes and then unloaded to ~ 70 MVA when the Graham 345/138 kV was returned to service.  1800_C has a continuous rating of 84 MVA.  Curtailing flow at Oklaunion and opening the Graham Tr. were actions identified earlier that day to mitigate flow on the remaining 138 kV feed to the north from the Graham station.  The loss of additional transmission equipment may have invalidated the switching plan.

At 09:01 Bowman Switch to Graham 345 kV line 6015_A, carrying 56 MW and 138 kV line 6155_A, carrying 8 MW tripped.  The reported cause was a helicopter coming into contact with a static wire.  The static wire wrapped around the 345 kV line.  The 138 kV line reclosed, but was deenergized to perform maintenance on the 345 kV line. The 345/138 kV transformer also tripped, as it is connected to the line side of the Graham – Bowman 345 kV circuit breaker.

At 12:30, a Maintenance Level 1 outage was taken on Okalunion circuit breaker 5635 to repair an SF6 leak.  The maintenance was scheduled to last until 18:30 on 6/24.  Opening this breaker opens the ring bus between the Abilene Mulberry Creek 345 kV line and the North DC tie.

No ratings were exceeded and contingency analysis results showed no post contingency loading problems.  Study cases were run to analyze the outage of Fisher Road Switch to Oklaunion at higher loads in order to mitigate post contingency loading on the remaining 138 kV path north from Graham and the 138 kV system around Oklaunion.  The corrective actions identified included reducing generation at Oklaunion and flow on the North DC tie, raising generation at Wichita Falls, and opening the 345/138 kV transformer at the Graham station.

TXU ED restored the Bowman Switch to Graham 345 kV line 6015_A at 18:45 and the Switch to Graham 138 kV line 6155_A at 18:52.  AEP transmission restored the 345/138 kV transformer at Oklaunion at 20:45.  AEP transmission reports damage on the Fisher Road – Oklaunion 345 kV line 6011_B and has forced the line out until 18:30 on 6/25. Lightning arrestors were identified as the cause of the line relaying out of service.  The Bowman – Fisher Road - Oklaunion circuit had previously tripped during inclimate weather on 5/31 at 21:17 and was returned to service by 00:20 on 6/1.

With the system configuration of Oklaunion – Fisher Road 345 kV and both 345 kV and 138 kV lines from Graham to Bowman out of service, approximately 480 MW of load was exposed to the single contingency of the loss of the remaining 345 kV line into the area from Jacksboro to Bowman, carrying roughly 377 MW during the event.  Had this contingency occurred, the only resources available remaining are the Wichita Falls cogeneration facility and 2 138 kV lines.  Four units were on line at Wichita Falls with a total maximum capacity of 80 MW.  The Graham – Arrowhead line, importing 77 MW to the pocket, has multiple segments with the lowest continuous rating of 136 MVA.  Arrowhead – Newman, rated at 200 MVA, was exporting about 25 MW.

6/25	00:48	138 kV bus outage at Olinger cleared the 138/69 kV transformer, along with circuits to Ben Davis 1 & 2, Firewheel, and Swindall.

6/28  16:11 – 16:40	ERCOT experienced low frequency (59.92 – 59.94) and had exhausted the available 815 MW of Up Regulation.  The QSE with the negative SCE and 1300 MW unconstrained spinning was contacted at 16:20 and requested to correct the SCE.  ERCOT was informed that the generation was not available due to gas problems at multiple plants.  The QSE was requested to update the Resource Plan at 16:30 and adjusted the plan at 16:40.  A second QSE showing an availability of 1000 MW was issued a 500 MW VDI at 16:34.  The QSE initially reported the generation was unavailable but replied at 16:36 that they could provide the 500 MW.