# The attached document is intended to fulfill the requirements of the NERC Planning Standard I.F., found on pages I-53 through I-66.

Revised: 11/16/98

# Revised:  2/19/99

# APPENDIX V.C. – DISTURBANCE MONITORING REQUIREMENTS

## INTRODUCTION

Disturbance monitoring is necessary to determine the performance of the electric system and protective relaying, to verify system models, and to determine the causes of system disturbances. To ensure that adequate data is available for these activities, the disturbance monitoring requirements and procedures discussed in this document have been established for ERCOT.

Disturbance monitoring equipment includes digital fault recorders (DFR’s), certain protective relays with fault recording capability, and dynamic disturbance recorders (DDR’s). Sequence-of-event recorders (SER’s) are also considered disturbance monitoring equipment. SER’s are not required, as they provide limited information and have largely been replaced by digital fault recorders and microprocessor-based protective relays.

There are no equipment requirements specified in this document for generation owners that are not also transmission providers, but there may be other requirements to install such equipment (interconnect agreements, etc.)

## FAULT RECORDING EQUIPMENT

Fault recording equipment includes digital fault recorders (DFR’s) and protective relays with fault recording capability meeting the triggering requirements below.  Fault recording equipment should be time synchronized when practical.

Triggering Requirements:

Fault recording equipment triggering must occur for system voltage magnitude and current magnitude disturbances (ΔV and ΔI) without requiring any circuit breaker operations or trip outputs from protective relay systems. Triggering by additional methods is acceptable. Triggering shall be adjusted to operate for faults in the area to be monitored, which should overlap into the area of coverage of adjacent fault recorders.

Location Requirements:

The location criteria below shall apply to equipment operated at or above 100 kV. Fault recording equipment in the form of DFR’s or fault recording protective relays must be installed at the following facilities as a minimum:

- Interconnections to other Regions (i.e. outside ERCOT).

- Switching stations where electrical transfers of equipment can be made between ERCOT and another Region.

- Switching stations having three or more non-radial 345 kV line terminals.    If a switching station is one bus removed from a station with a larger number of line terminals, then the fault recorder shall be located at the larger station and not required at the smaller station.

4) Switching stations that are more than one breakered bus away from a fault recorder and have five or more non-radial line terminals.

5)	For the purpose of evaluating #3 and #4 in this section, autotransformer or generating capacity totaling 150 MVA or greater (based upon minimum nameplate rating upon which transformer impedance is stated, i.e., base rating) shall constitute a non-radial line terminal at the highest voltage level to which it is directly connected.

### APPENDIX V.C. – DISTURBANCE MONITORING REQUIREMENTS

Data Recording Requirements:

The following quantities must be recorded for equipment operating at 100 kV or above at facilities where fault recording equipment is required:

- Two sets of voltages for breaker-and-a-half and ring bus substation configurations.    One set of voltages for each bus in other substation configurations.    A set of voltages shall consist of each phase voltage waveform and the residual voltage waveform.

- For all lines, neutral (residual) current waveform.

- Status – circuit breaker positions.

- Status – circuit breaker trip circuit energization.

- Date and time stamp (CST).

For all new or upgraded fault recorder installations, the following additional items must also be recorded:

- For all autotransformers, current waveform for three phases and either neutral / residual current waveform or current waveform in delta windings.

- For all lines, two phase current waveforms.

- Status – carrier transmitter control, i.e. start, stop, keying.

- Status – carrier received.

Data Reporting Requirements:

Fault data shall be reported to the ERCOT ISO at least annually for compilation into a database. Data shall be reported for all 345 kV system faults. When an Entity has data from multiple recorders for a single event, only data from the best recording (usually the closest recorder) is required.

This data shall be submitted in the form of a computer file or files. Two formats are acceptable for data submissions. One format shall be COMTRADE fault recordings (.cfg and .dat files) and one or more associated text files that associate the COMTRADE recordings with system disturbances and ERCOT short circuit database bus numbers. The second format shall be a Microsoft Excel spreadsheet or comma delimited ASCII text that can be read into a Microsoft Excel spreadsheet. For this second format, the data fields to be reported for each record, in the following order, are:

Reporting Entity

Faulted Circuit 		Circuit or Bus (1, 2, A, B, N, S, etc.)

From Bus (ERCOT short circuit database bus number)

To Bus (ERCOT short circuit database bus number)

Nominal Voltage of Faulted Branch or Bus (kV)

Physical Fault Location in Percent from “From Bus” (if physical location found, i.e. not calculated location)

Date (CST, MM/DD/YYYY)

Time (CST, HH:MM:SS, 24 hour format)

Cause Code

Fault Recorder Data	Circuit (1, 2, A, B, N, S, etc.)

From Bus – Recorder Location (ERCOT short circuit database bus number)

To Bus – Monitored branch (ERCOT short circuit database bus number)

Nominal Voltage of Monitored Branch (kV)

Measured Current Magnitude (primary value in RMS amperes)

Recorded Fault Duration (cycles)

Fault Type (using reporting entity’s phase designations – AB, CG, etc.)

### APPENDIX V.C. – DISTURBANCE MONITORING REQUIREMENTS

Optional Comments (40 char. max.)

The database compiled by the ISO shall be made available to all ERCOT members for verifying and improving system models, or analyzing system disturbances. Submitted data will be retained by the ISO for a minimum of one year.

Fault records shall be provided to ERCOT and NERC upon request, along with channel identification and scaling information to allow analysis of the records. Fault records shall be retained and made available for at least one year from the date the record was made. Fault records shall be shared between entities, upon request, for the analysis of system disturbances.

Maintenance and Testing Requirements:

Fault recording equipment must be properly maintained and tested in accordance with the manufacturer’s recommendations. Calibration of the analog (waveform) channels shall be performed at least every five years and documented. Fault recording equipment must be operationally tested at least annually to ensure that the equipment works. A successful operational test is defined either as the equipment producing a record triggered by a power system disturbance or as the equipment producing a manually triggered record.

## DYNAMIC DISTURBANCE RECORDING EQUIPMENT

(ES to complete this section)

## EQUIPMENT REPORTING REQUIREMENTS

ERCOT members shall maintain a current database list describing the disturbance monitoring equipment installed to meet the location requirements of this document and provide ERCOT with this list at least annually and upon request (within 30 days). The ERCOT ISO shall maintain a database containing this information and update it at least annually. Each transmission provider shall maintain a current database list describing all disturbance monitoring equipment installed and shall provide this information to ERCOT and NERC on request (within 30 days).

Although there are no equipment requirements stated, generation owners shall maintain a current database list describing all disturbance monitoring equipment installed and shall provide this information to ERCOT and NERC on request (within 30 days).

The database lists shall include installation location, type of equipment, make and model of equipment, operational status, and a listing of the major equipment being monitored.

## REVIEW PROCESS

Fault recorder and disturbance recorder locations shall be reviewed by ERCOT for compliance and adequacy when significant changes are made to the transmission system or at least every five years.

The requirements set forth in this document must be reviewed for adequacy by ERCOT at least every five years. Date of last review: xx/xx/xxxx.