C.	SYSTEM PROTECTIVE RELAYING

1.	Introduction

The satisfactory operation of the ERCOT System, especially under abnormal conditions, is greatly influenced by the Protective Relay Systems (PRS) in effect in individual power systems. PRS are defined as the protective relays, associated communications system, voltage and current sensing devices, and the DC system up to the terminals in the circuit breaker.  Although relaying of tie points between utilities is of primary concern to the ERCOT System, internal relaying often directly, or indirectly, affects the adjacent area also.  Individual equipment owners have an obligation to implement relay application, operation, and preventive maintenance criteria that assure the highest practicable reliability and availability of service to the ultimate power consumers of the concerned area and neighboring areas.  PRS of individual equipment owners shall not adversely affect the stability of system interconnections.  Minimum PRS requirements are outlined in NERC Planning Standards.

These objectives and design practices shall apply to all new protection systems.  It is recognized that there may be portions of the existing System which do not meet these objectives.  It is the responsibility of individual companies to assess the protection systems at these locations and to make any modifications that they deem necessary.  Similar assessment and judgment should be used with respect to protection systems existing at the time of revisions to this guide. Special local conditions or considerations may necessitate the use of more stringent design criteria and practices.

2.	Design and Operating Requirements for All Facilities

- PRS shall be designed to provide reliability, a combination of dependability and security, so that PRS will perform correctly to remove faulted equipment from the power system.

- For planned system conditions, protection systems shall be designed not to trip for stable swings which do not exceed the steady-state stability limit.  Note that when out-of-step blocking is used in one location, a method of out-of-step tripping should also be considered. PRS shall not interfere with the operation of the ERCOT System under the procedures identified in the other Operating Guides.

- Any loading limits imposed by PRS shall be documented and followed as a system operating constraint.

- The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even under first-contingency conditions.

- Applicable IEEE/ANSI guides shall be considered when applying PRS on the ERCOT System.

- The planning and design of generation, transmission and substation configurations shall take into account PRS requirements of dependability, security and simplicity.  If configurations are proposed that require PRS that do not conform to this guide or to accepted IEEE/ANSI practice, then the entities affected shall negotiate a solution.

- All entities shall give sufficient advance notice of any power system changes that could require changes in PRS.

- Power system operators shall be familiar with the purposes and limitations of PRS.

- The design, coordination, and maintainability of all existing PRS shall be reviewed periodically to ensure that the systems continue to meet power system requirements.  This review shall include the need for redundancy.  Where redundant PRS are required, separate AC current inputs and separately fused DC control voltages shall be provided with the upgraded PRS.  Documentation of the review shall be maintained and supplied to ERCOT and NERC on request within 30 days.  This documentation shall be reviewed by ERCOT for verification of implementation.

- Upon request, within 30 days, generating equipment owners shall provide the ERCOT ISO with the operating characteristics of any generator’s equipment PRS or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

- Upon request, within 30 days, generating equipment owners shall provide ERCOT ISO with information that describes how generator controls coordinate with the generator’s short-term capabilities and PRS.

- Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation only operates for failure of the voltage regulator/limiter.  Documentation of coordination shall be supplied to ERCOT upon request within 30 days.

- Special Protection Systems (SPS) are PRS designed to detect abnormal system conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable system performance.  SPS actions include among others, changes in demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable facility loadings.  If used:

- SPS shall be automatically armed when appropriate.

- The status indication of any automatic or manual arming of SPS shall be provided as SCADA alarm inputs.

- SPS shall be designed in accordance with the intent of this Operating Guide when they are required to prevent adverse effects outside the local area.

- The owner(s) of existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

- ERCOT shall conduct a review of proposed or modified SPS before the SPS is placed in service.  This review shall verify that the SPS complies with ERCOT and NERC criteria and guides.  The review shall include system studies verifying that failure of a single component of the SPS, which would result in failure of the SPS to operate when required, would not result in cascading transmission outages.  The review shall also verify that misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, shall meet the system performance requirements of categories A, B, and C of Table I of NERC Planning Standard I.A.  This review shall be documented and the documentation provided to NERC on request within 30 days.

- ERCOT shall conduct a review of existing SPS every five years or as required by changes in system conditions.  This review shall verify that the SPS complies with ERCOT and NERC criteria and guides.  The review shall evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required.  The review shall also evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, and without any other system contingency.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within 30 days.

- SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures.

3.	Performance Analysis Requirements

a.	All power system disturbances (unwanted trips, faults, and PRS operations) shall be analyzed by the equipment owner promptly and any deficiencies investigated and corrected.

- All PRS misoperations shall be documented, including corrective actions and the documentation supplied to ERCOT and NERC upon request within five business days.  All PRS misoperations shall be documented using “Relay Misoperation Report” Form 1.  The following events constitute a reportable PRS misoperation:

(1)	Failure to Trip – Any failure of a PRS to initiate a trip to the appropriate terminal when a fault is within the intended zone of protection of the device.

- Slow Trip – A correct operation of a PRS for a fault in the intended zone of protection where the relay system initiates tripping slower than the system design intends.

- Unnecessary Trip During a Fault – Any relay initiated operation of a circuit breaker during a fault when the fault is outside the intended zone of protection.

- Unnecessary Trip Other Than Fault – The unintentional operation of a PRS which causes a circuit breaker to trip when no system fault is present.  May be due to vibration, improper settings, load swing, or bad order relays.

- Failure to Reclose – Any failure of a PRS to automatically reclose following a fault if that is the design intent.

###### FORM 1

| DATE : | TIME: | UTILITY: | VOLTAGE: |
| --- | --- | --- | --- |
| RELAY TYPE: STYLE #: | CB NUMBER: | LINE/BUS/AUTO NAME : |  |
| FLAGS : | MANUFACTURER : |  |  |
| Description of Misoperation/Failure: |  |  |  |
| (80 Character) |  |  |  |
| Investigation Results: |  |  |  |
| (80 Character) |  |  |  |
| Corrective Action: |  |  |  |
| (80 Character) |  |  |  |
| Target Date: |  |  |  |
| Recommendations: |  |  |  |
| Reported By: |  |  | Date: |
| Phone Number: |  |  |  |

c.	All equipment owners shall participate in the sharing of information regarding performance of PRS upon request.

- At least annually, ERCOT shall review the PRS misoperations reports of equipment owners for analysis of PRS performance and compliance.

- All equipment owners shall install, maintain, and operate disturbance monitoring equipment in accordance with the requirements in ERCOT Guides Appendix V.B.

- Transmission PRS owners shall provide an assessment of the system performance results of simulation tests of the contingencies in Table I of the NERC Planning Standard I.A.  These assessments should be based on existing protection systems and any existing backup or redundancy protection systems to determine that existing transmission protection systems are sufficient to meet the system performance levels as defined in NERC Planning Standard I.A. and the associated Table I.  All non-compliance findings shall be documented, including a plan for achieving compliance.  These assessments shall be provided to NERC and ERCOT on request within 30 days.

4.	Maintenance and Testing Requirements

- Each new or modified protective relay system shall be thoroughly tested and proper operation verified prior to placing the equipment in its zone of protection in service.

- PRS owners shall have documented protection system maintenance and testing programs in place.  Documentation shall include identification of protection systems, a summary of testing procedures including requirements for frequency of tests, and the date last tested.

- PRS shall be maintained by periodic testing and inspection of all components to assure continued reliability.  Identified deficiencies shall be corrected.  Documentation demonstrating compliance with the owner’s maintenance and testing programs shall be supplied to ERCOT and NERC upon request within 30 days.

5.		Facility Requirements and Recommendations

a.		General Protection Criteria

-

(1)	Dependability

(a)	Except as noted in Sections (1).(d) and (1).(e) below, all elements of the System (i.e., lines, buses, transformers, generators, breakers, capacitor banks, etc.) shall be protected by two protection systems, each of which is independently capable of detecting and isolating all faults thereon, without undue disturbance to the Bulk Power System.

(b)	The protection system design should avoid the use of components common to the two systems.  Areas of common exposure should be kept to a minimum to reduce the possibility of both systems being disabled by a single contingency.

(c)	The use of two identical protection systems is not generally recommended, due to the risk of simultaneous failure of both systems because of design deficiencies or equipment problems.

(d)	Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.  This protection need not be duplicated.

(e)	On installations where free-standing or column-type current transformers are provided on one side of the breaker only, protection should be provided to detect a fault on the primaries of such current transformers.  This protection need not be duplicated.  Application of free-standing CTs requires extra care to ensure that the relaying is proper and that the schemes overlap.

(2)	Security

Protection systems should be designed to isolate only the faulted element, except in those circumstances where additional elements should be tripped intentionally to preserve system integrity.  For faults external to the protected zone, each protection system should be designed to either not operate, or to operate selectively with other systems, including breaker failure.  (In this context, the limits of the protected zone are defined by the circuit breakers.)

(3)	Dependability and Security

(a)	Protection systems should be no more complex than required for any given application.

(b)	To the maximum degree practicable, the components used in protection systems should be of proven quality, as demonstrated either by actual experience or by stringent tests under simulated operating conditions, to ensure that the reliability of the protection systems is not degraded by the components.

- (c)	Protection systems shall be designed to minimize the possibility of component failure or malfunction due to electrical transients and electromagnetic interference or external effects such as vibration, shock and temperature.

(d)	Critical features associated with protection system and circuit breaker operation shall be annunciated or monitored.

(e)	Protection system circuitry and physical arrangements shall be carefully designed so as to minimize the possibility of incorrect operations due to personnel error.

(f)	Computerized fault studies shall be used during the planning or design stages to analyze the effects of an addition or modification to the system and to determine proper relay coordination.

(4)	Operating Time

The objective of System protection is to take corrective action in the shortest practical time with due regard to selectivity, dependability and security. In cases where clearing times are deliberately extended, consideration should be given to the following:

(a)	Effect on system stability or reduction of stability margins.

(b)	Possibility of causing or increasing damage to equipment and subsequent extended repair and/or outage time.

(c)	Effect of disturbances on service to customers and neighboring utilities.

(5)	Protection System Testing and Maintenance

(a)	The design of protection systems both in terms of circuitry and physical arrangement shall facilitate periodic testing and maintenance.  Test devices or switches should be provided to eliminate the necessity for removing or disconnecting wires during periodic testing.

(b)		Commissioning of new equipment should consist of the following steps:

- Relay installation wiring diagrams cross-checked against schematics

- After completion of construction, physical check of wiring and relay installation

- Check and testing before energizing of all equipment in the zone of protection, including relay testing.  It is desirable to test the relays at the setting the relay will have in service

- Check of supporting paperwork, such as relay test reports

- Check that relays physically agree with the relay settings

- Check that proper settings have been made

- Written record of trip check and energize procedure

- In-service measurement of voltage and current magnitudes and phase angles, and comparison to expected values and to other instrumentation

- Release to system operations for service

(6)	Analysis of System Performance

(a)	Relay operation and settings shall be reviewed periodically and whenever significant changes in generating sources, transmission facilities, or operating conditions are anticipated.

(b)	Sequence of events recorders, fault recorders, dynamic disturbance recorders, fault locators, etc., should be installed to the maximum practicable extent to permit analysis of system disturbances and protection system performance.  It is recommended that these devices be time synchronized when possible.  Also see ERCOT Guides Appendix V.B. – Disturbance Monitoring Requirements, Location Requirement.

(c)	Naturally-occurring faults and other system disturbances should be analyzed as a source of information as to the health of relay schemes in the System.  Sources of information usually available are:

- Short circuit study for the exact conditions of the fault

- Fault recorder traces

- Sequence of events data recording the opening and closing of contacts in the protective relay scheme and associated communication equipment

- Fault locator data

- SCADA (Supervisory Control And Data Acquisition) logger output of breaker operation and alarms

- Interviews with operating personnel and/or other witnesses

- Field report of relay flags and breaker counter changes

- Field report of the fault location, if found

- Records of relay setting, relay testing, trip check and energize procedures as carried out, in-service measurements, relay wiring diagrams and schematics, manufacturers' information

- Other co-workers and System Protection Task Force members

- Manufacturers' application and design engineers

(d)	Steps one can follow in analyzing a disturbance are:

- Gather data

- Create a time line consisting of events and periods between events

- Compare actual and calculated values of current and voltage during the periods between events

- Compare actual and expected breaker operations and flags

- e)	Choose the least complicated explanation for contradictory information and to fill in missing information

- Gather additional information as indicated to prove or disprove explanations

- Iterate

- Document by issuing a report of all findings, changes, and recommendations

- After a reasonable time, check back to see if the recommendations have been carried out

b.	Equipment and Design Considerations

(1)	Current Transformers

(a)	Current transformers (CTs) associated with protection systems shall have adequate steady-state and transient characteristics for their intended function.

(b)	The output of each current transformer shall remain within acceptable limits for the connected burdens under all anticipated fault currents to ensure correct operation of the protection system.

(c)	Current transformers or their secondary windings shall be located so that adjacent protection zones overlap.

(d)	Current transformer secondary wiring shall be grounded at only one point. When multiple current transformers are interconnected, the combination shall have only one ground.

(e)	Other considerations:

- Internal bushing CTs are preferred over external slip-over CTs

- 10L800 (C800) class CTs are preferred for relaying

- Breakers and free-standing CTs with four or more sets of CTs are preferred

- Over-the-bushing external CTs can sometimes solve problems when there aren't enough CTs.  Note that there may

be an unprotected region between the external CT and the bushing CT.

- Shorting type terminal blocks should be provided for all CTs

(2)	Voltage Transformers and Potential Devices

(a)	Voltage transformers (VTs) and potential devices associated with protection systems shall have adequate steady-state and transient characteristics for their intended functions.

(b)	Voltage transformers and potential devices shall have adequate volt-ampere capacity to supply the connected burden while maintaining their relay accuracy over their specified primary voltage range.

(c)	Usually one set of VTs (with two separate secondary windings per VT) per bus (i.e. single bus substation configuration) or per power system element (i.e. ring bus and breaker-and-a-half substation configurations) is sufficient.  The two systems protecting a power system element may use separate secondary windings of the VTs or one of the secondary windings may be dedicated to supplying the polarizing potential and the other winding used to supply other protection and monitoring functions.

(d)	Voltage transformer and potential device secondary wiring shall be grounded at only one point.  (ANSI/IEEE C57 recommends grounding at the panel.)

(e)	Voltage transformer installations shall be designed with due regard to ferroresonance due to capacitance across the interrupter at 138kV and above.

(f)	Other considerations

- Special attention should be given to the physical properties of secondary circuit fuses

- Capacitor coupled voltage transformers are suitable for relaying and SCADA telemetry

- Report loss of VT voltage (VT fuse failure) over SCADA

(3)	Batteries and Direct Current (DC) Supply

(a)	DC batteries associated with System protection shall have a high degree of reliability.

(b)	Two batteries each with its own charger should be provided at each location.  An acceptable alternative is one battery with two separately

protected branches.  The systems protecting a zone shall be supplied from the separate sources or branches. For a new facility, two batteries shall be required in locations that remote backup clearing of lines and substation faults is not achieved. Where only one battery is used, remote backup clearing of line and substation faults is required.

(c)	Each battery shall have sufficient capacity to permit operation of the station, in the event of a loss of its battery charger or the AC supply source, for the period of time necessary to transfer the load to the other battery or to re-establish the supply source.

Each battery and its associated charger shall have sufficient capacity to supply its share of the DC load of the station.

(d)	A fault at the battery terminals can only be interrupted by a mid-bank protective device.  If a mid-bank protective device is not used, then the connections between the battery terminals and the main protective devices shall possess the highest possible degree of reliability.

(e)	The battery chargers and all associated circuits shall be protected against short circuits.  All protective devices shall be coordinated to minimize the number of DC circuits interrupted.

(f)	The regulation of DC voltage shall be designed such that, under all possible loading conditions, voltage within acceptable limits will be supplied to all devices.

(g)	DC systems shall be monitored to detect abnormal voltage levels, both high and low, DC grounds, and loss of AC to the battery chargers.  Loss of DC to relay schemes shall be alarmed.  Also, where possible the loss of AC to the battery chargers and loss of DC should be provided as SCADA alarm inputs.

(h)	DC systems shall be designed to minimize AC ripple and voltage transients.

(i)	The DC circuit protective devices used shall have published DC interrupting ratings suitable for the required circuit duty.

(4)	AC Auxiliary Power

(a)	There should be two sources of station service AC supply, each capable of carrying all the critical loads associated with protection systems.

(b)	Failure of station service AC supply should be alarmed over SCADA.

(5)	Circuit Breakers

(a)	Two trip coils, one associated with each protection system, shall be provided for each operating mechanism.  The failure of one coil shall not damage or impair the operation of the other coil.

(b)	The design shall be such that the breaker will operate if both trip coils are energized simultaneously, or either trip coil alone, and verified by tests.

(c)	Circuit breaker auxiliary switches used in protection systems should be highly reliable with a positive make-break action and good contact wipe.  Multiplier contacts simulating breaker auxiliary switches should be used with caution in protection systems.

(d)	A three-phase and line-to-ground interrupting study to validate or indicate breaker interrupting rating shall be performed.

(6)	Communications Channels

(a)	Where communication channels are required for protection purposes, the communication facilities shall have a degree of reliability no less than that of the other protection system components.  For extra security, the output contacts from two independent channels may be wired in series.

(b)	Where communication channels are required in each of the two protection systems, the channels shall be separated physically and designed to minimize the risk of both channels being disabled simultaneously by a single contingency.

(c)	Communication channels shall be provided with means to verify signal performance.

(d)	Other considerations

- Report loss of channel over SCADA

- Automatic testing of power line carrier (PLC) is desirable to reduce false trips from failure to block

- Split up PLC loads between DC sources so that loss of one fuse does not disable all the carrier sets.  If all the carrier sets were to be disabled, then multiple false trips during a fault could result.

(7)	Control Cables and Wiring

(a)	Control cables, wiring and auxiliary control devices should be such as to assure high reliability with due consideration to published codes and standards, fire hazards, current-carrying capacity, voltage drop, insulation level, mechanical strength, routing, shielding, grounding and environment.

(b)	Other considerations

- Shielded cable may be necessary for certain relay and SCADA applications

- AC or DC go-and-return functions should be implemented in the same cable to avoid induction loops

- Individual wires in cables should have colored jackets, not black jackets with a "color" printed on the jacket

- Standardization of the relationship between wire colors and functions is desirable

- No splice in any wire or cable

- All cables terminated on terminal blocks

(8)	Environment

(a)	Means shall be employed to maintain environmental conditions that are favorable to the correct performance of protective relays.  Particular attention should be given to solid state equipment installations.

- Other environmental hazards to look out for:

  - Fire ants

  - Rats

  - Snakes

  - Dust, dirt, grime

  - Trash and leftover hardware

  - Water

  - Gunfire

  - Theft of substation and transmission grounds

  - Hand-held radio keyed near solid-state relays

  - Batteries located in same room as relays (battery fires)

c.	Specific Application Considerations

(1)	Transmission Line Protection

(a)	Each of the two independent protection systems shall detect and initiate action to clear any line fault without undue system disturbance.  The protection systems shall operate for line faults so that, if ultimate clearing should be accomplished by a breaker failure scheme,  a widespread disturbance will not result.  A protection system, which can operate for faults beyond the zone it is designed to protect, shall be selective in time with other protection systems, including breaker failure.

-

- Transmission line protection should consist of:

- Primary phase and ground protection over a communications channel

- Backup relaying with at least two zones of phase protection

- Backup relaying with at least two zones of ground protection, or backup relaying with ground directional overcurrent relaying (time delay and instantaneous)

- "Ground chain protection" to recognize and trip for a three- phase fault right at the terminals, in service for a short period of time just as the line is energized, for lines with line side VTs

- Recognition and trip for open conductor is desirable but not required

- Overload protection is provided by SCADA analog alarms and dispatcher discretion

- Fault detector relays to supervise phase distance relaying to prevent inadvertent trip due to VT failure

- Short lines may require special attention, such as dual primary schemes, etc.

- Fuses shall not be used in the 3Vo polarizing supply for ground relays

(2)	Transmission Station Protection

(a)	Each zone in a station shall be protected by two independent protection systems.  For zones not protected by line protection, at least one of the two systems shall be a differential type.

(b)	The protection systems shall be designed to operate for station faults so that, if ultimate clearing is accomplished by a breaker failure scheme, a widespread disturbance will not result.  The protection systems shall be designed to operate properly for the anticipated range of currents.

(c)	Station protection should consist of:

- Bus differential or bus overcurrent protection of all buses

  - All transformers protected by transformer differential, transformer overcurrent, or fuses (for small transformers).  Note that ferroresonance is possible for fused transformers above 69kV.

  - Sudden pressure relay protection for transformer main tanks and transformer tap changer compartments

(3)	Breaker Failure Protection

(a)	Breaker failure protection should be provided to trip all necessary local and remote breakers in the event that a breaker fails to clear a fault.

(b)	The breaker failure protection should be initiated by each of the protection systems which trip that breaker.  It is not necessary to duplicate the breaker failure protection itself.

(c)	Induction cup or solid state fault current detectors shall be used to determine if a breaker has failed to interrupt.

(d)	Plunger or clapper type overcurrent relays are not recommended as breaker failure fault detectors.

(4)	Generator Protection

(a)	Generator faults shall be detected by more than one protection system.  These may include faults in the generator or generator leads, unit transformer, and unit-connected station service transformer.

(b)	Generators shall be protected to keep damage to the equipment and subsequent outage time to a minimum.  In view of the special consideration of generator unit protection, the following are some of the conditions that should be detected by the protection systems:

  - (a)	Unbalanced phase currents

  - (b)	Loss of excitation

  - (c)	Over-excitation

  - (d)	Field ground

  - (e)	Inadvertent energization (reverse power)

  - (f)	Uncleared system faults

  - (g)	Off-frequency

It is recognized that the overall protection of a generator will also involve non-electrical considerations.  These have not been included as part of this criteria.

(c)	The apparatus shall be protected when the generator is starting up or shutting down as well as running at normal speed; this may require additional relays as the normal relays may not function satisfactorily at low frequencies.

(d)	A generator facilities shall not be tripped for a system swing condition except when that particular generator is out of step with the remainder of the system.  This does not apply to protection systems designed to trip the generator as part of an overall plan to maintain stability of the power system.

(e)	The loss of excitation relay shall be set with due regard to the performance of the excitation system.

(5)	Automatic Underfrequency Load Shedding Protection Systems

(a)	Automatic under-frequency load shedding systems are not generally located at bulk power system stations; however, they have a direct effect on the operation of the System during major emergencies.

(b)	The criteria for the operation of these protection systems are detailed in Operating Guide I.F. - Application of Under-frequency Relaying.

(c)	Automatic under-frequency load shedding protection systems need not be duplicated.

(d)	Generator and turbine under-frequency protection systems where applicable shall be coordinated with Operating Guide No. I.F. - Application of Under-frequency Relaying.  If the generator and turbine under-frequency protection systems cannot be coordinated with Operating Guide I.F., this shall be reported to and reviewed by the ERCOTReliability and Security Subcommittee.

(e)	On pressurized water reactor steam supply units where under-frequency related protection systems are installed to detect loss of coolant flow condition, these protection systems shall be coordinated with the automatic under-frequency load shedding program.

(6)	Automatic Under-voltage Load Shedding Protection Systems

Required by NERC – To Be Developed