G.	EMERGENCY ELECTRIC CURTAILMENT PLAN (CONT.)

### CONDITION 1 - MAINTAIN ERCOT RESPONSIVE RESERVE OBLIGATION

- CONTROL AREAS	Order the GENERATION AND LOAD ENTITIES to:

- -  Order needed available units on line.

- -  Utilize non-ERCOT resources as available.

     ISO	-  Request utilization of all needed available units.

-  Distribute available spinning reserves among Control Areas up to maximum transfer capability.

-  Obtain emergency energy over the DC tie(s) after all available generation within ERCOT has been utilized.

- -  Notify the Southwest Power Pool Security Coordinator.

CONDITION 2 - MAINTAIN ERCOT SPINNING RESERVE EQUAL TO LARGEST UNIT IN OPERATION

-     ISO			- 	Direct Deficit Control Areas with available interruptible load to remove sufficient interruptible load in amounts specified by the ISO to eliminate their deficit condition and restore adequate regulation.

- CONTROL AREAS          	Direct DEFICIT LOAD ENTITIES to:

- Remove sufficient interruptible load, including loads controlled by high-set under-frequency relays, to conform with ISO instructions.

- -	Reduce customer loads by load management if available.

- Reduce customer loads by reducing distribution voltage if deemed beneficial by the Host Control Area.

- CONDITION 3

- CONTROL AREAS	   Direct ALL LOAD ENTITIES to:

-  Remove increments of interruptible load that are not controlled by high-set under-frequency relays.

- -  Reduce in-house non-essential loads.

- CONDITION 4

- CONTROL AREAS	   Direct ALL LOAD ENTITIES to:

- -  Remove all remaining increments of interruptible loads.

- CONDITION 5

-     CONTROL AREAS          	Direct DEFICIT LOAD ENTITIES to:

- Utilize other resources outside ERCOT by implementing block load transfer schemes.

-  Request voluntary curtailment of large industrial customers.

-  Appeal by media for voluntary load reduction.

-     ISO		- Redistribute available spinning reserves among Control Areas up to maximum transfer capability.

93