## ERCOT OPERATING GUIDE NO. III

# EMERGENCY OPERATION

## F.	SHORT SUPPLY OPERATIONS

The ERCOT ISO will review projected conditions and will notify Control Areas when a capability short supply (available generating capability will not meet forecast peak loads and responsive reserve obligations) is possible.  Upon notification, Control Areas will notify each Generating and Load Entity within its area and will review their particular situation and report back if any corrective actions can be taken.

1.	SHORT SUPPLY ADVISORY

If after confirming that the forecasted conditions still indicate that short supply conditions are highly probable, the ISO will issue an ERCOT Short Supply Advisory.  Upon notification of this advisory, each Control Area and Load Entity will prepare to implement applicable steps of the Emergency Electric Curtailment Plan (EECP).

a.	General Preparation

All ERCOT Control Areas and Load Entities will take appropriate preparation measures when the ISO declares a Short Supply Advisory.  The preparation measures should include at least the following:

	Verify that all generation and/or fuel resources, and transmission lines are being prepared for emergency operation;

	Plan the removal of non-essential in-house loads;

	Plan the removal of interruptible load as needed;

	Notify appropriate authorities and Company management

	Notify key employees of "call out" requirements for emergency operations;

	Keep the ISO informed of your state of preparedness;

	Be prepared to implement all other steps of the EECP.

b.	Deficit Load Entities

A Load Entity that is forecast to be deficit and a contributor to the ERCOT Short Supply Advisory condition should take the following actions (which take considerable lead time to implement) to be in effect during the anticipated time of the deficiency:

	Plan the reduction of voltage to distribution customers as required by EECP condition 2;

	Request that large industrial customers voluntarily reduce in-house loads;

	Arrange for the transfer of load to resources outside of ERCOT where applicable;

	Appeal through the media for voluntary load conservation by customers.

88

F.	SHORT SUPPLY OPERATIONS (CONT.)

c.	Control Areas

If the ERCOT ISO forecasts that Condition 6, 7 or 8 of the EECP is likely when the Short Supply Advisory is in effect, all Control Areas shall implement the actions outlined in b. above.

89

# ERCOT OPERATING GUIDE NO. III

# EMERGENCY OPERATION

G.	EMERGENCY ELECTRIC CURTAILMENT PLAN (CONT.)

### CONDITION 1 - MAINTAIN ERCOT RESPONSIVE RESERVE OBLIGATION

- CONTROL AREAS	Order the GENERATION AND LOAD ENTITIES to:

- -  Order needed available units on line.

- -  Utilize non-ERCOT resources as available.

    ISO		-  Request utilization of all needed available units.

-  Distribute available spinning reserves among Control Areas up to maximum transfer capability.

-  Obtain emergency energy over the DC tie(s) after all available generation within ERCOT has been utilized.

- -  Notify the Southwest Power Pool Security Coordinator.

CONDITION 2 - MAINTAIN ERCOT SPINNING RESERVE EQUAL TO LARGEST UNIT IN OPERATION

- CONTROL AREAS          	Direct DEFICIT LOAD ENTITIES to:

-  Remove all interruptible loads, including loads controlled by high-set under-frequency relays.

- -	Reduce customer loads by load management if available.

- - Reduce customer loads by reducing distribution voltage if deemed beneficial by the Host Control Area.

- CONDITION 3

- CONTROL AREAS	   Direct ALL LOAD ENTITIES to:

-  Remove increments of interruptible load that are not controlled by high-set under-frequency relays.

- -  Reduce in-house non-essential loads.

- CONDITION 4

- CONTROL AREAS	   Direct ALL LOAD ENTITIES to:

- -  Remove all remaining increments of interruptible loads.

- CONDITION 5

-     CONTROL AREAS          	Direct DEFICIT LOAD ENTITIES to:

- Utilize other resources outside ERCOT by implementing block load transfer schemes.

-  Request voluntary curtailment of large industrial customers.

-  Appeal by media for voluntary load reduction.

-     ISO		- Redistribute available spinning reserves among Control Areas up to maximum transfer capability.

- 93

- CONDITION 6 - MAINTAIN 60.0 Hz (NO AVAILABLE SPINNING RESERVE) AND MAXIMUM TRANSFER LIMITATIONS

- CONTROL AREAS	   Direct ALL LOAD ENTITIES to:

- -  Reduce customer loads by load management if available.

- -  Reduce customer loads by reducing distribution voltage except when the Host Control Area deems it a threat to reliability or voltage stability.

- -  Request voluntary curtailment of large industrial customers.

- -  Utilize other resources outside ERCOT by implementing block load transfer schemes.

- -  Appeal by media for voluntary load reduction.

- - 	Confirm that all generators are at maximum generation and other   resources are being maximized.

93a