## Slide 1: PRR 586 Back-Cast
ERCOT Analysis
Presentation to WMS
April 22, 2005

## Slide 2: Observations
Ancillary Service Demand Factor (ASDF)
  15 minute summation of 1 minute intervals results in applying penalty to every 15 minute interval
ERCOT Frequency Control
  Metric would have to be modified to correlate acceptable frequency control (ERCOT CPS1) with QSE performance

## Slide 3: PRR586 Inputs & Assumptions
Back-cast of historical data for November 04
  Poorest ERCOT CPS1 Performance in Recent History
The total cost of Regulation Services for the month was $23 million (MCPC for URS & DRS multiplied by total obligation)
50% of the regulation service cost for a 15 minute interval is allocated when the penalty criteria is met
  The penalty criteria is (-1*ISCE*REGNm) where this is greater than zero
A tolerance dead-band is used that measures the aggregate sum of the QSEs ISCEs

## Slide 4: Results of the Analysis
Total penalty cost equaled $11.5 million for the month of November 04
The ASDF for all participants had at least 1 minute of the 15 minute sum in which an interval met the criteria for applying the penalty
Without a dead-band around an individual QSE’s ISCE, there is a risk of having a low ISCE and paying a large share of the penalty (i.e. if most QSEs have a ASDF = 0 in the interval)
ERCOT frequency was outside of the acceptable tolerance (+/-0.03 Hz dead-band) 11,460 one minute intervals out of a total of 43,200 one minute intervals.
  1/3 or 3,796 of the 11,460 intervals would not have had a penalty applied even though ERCOT frequency was outside an acceptable range, however, this can be addressed with a small change to the formula.

## Slide 6: Summary
A small change to the formula is needed so that QSE will not receive a good score when ERCOT is un-deploying regulation and the QSE is generating in an undesirable direction
Example of why this change is needed:
  REGNm (regulation need) = the one minute ERCOT deployed Regulation minus ERCOT Area Control Error (ACE)
  Example – ERCOT frequency = 60.00 Hz and ACE = 0 total deployed Regulation = -500 MW; (initial condition)
  Load increases 1 minute later -
  ERCOT frequency = 59.95 Hz; ERCOT ACE = -200 MW total deployed Regulation = -300 MW (un-deployed from 500 down to 300 down) ; QSEa is under generating and their SCE = -100 (hurting frequency)
  QSEa - REGNm = -300 – (-200) = -100
  QSEa - ASDF = (-1*-100*-100) = -10,000<0 = 0 (good score)

## Slide 7: Option Considered Under Current Proposal
Calculate the number of 1 minute intervals that meet the penalty criteria for one or more QSEs
  Approximately 48% of the intervals in the month met the penalty criteria

## Slide 8: Options Considered
Remove System-wide deadband and, instead
Apply deadband to individual QSEs
  Use L10 values from PRR 525
Modify ASDF from (-1*ISCE*REGnm) to (ISCE*ACE) to align the metric with ERCOT frequency
  Results in 35,901intervals out of 43,200 1 minute intervals in which the penalty criteria would be met by one or more QSEs

## Slide 9: Review of Uninstructed Resource Charge (URC)
Modify inputs to existing Uninstructed Resource Charge (URC) Calculation
  Advantages
    Uses revenue meter quality data
    Protocols allow Deadband modification
    Other inputs easily modifiable with Protocol Changes
    System design already in place
  Disadvantages
    Doesn’t apply penalty for under generating when MCPE is positive
    Based on 15 minute integration
    May not significantly address 0600 and 2200 ramp period scheduling
    This alternative does not satisfy Potomac Recommendation #11
Modify URC pricing language to apply an appropriate penalty price for over or under generating regardless of magnitude of MCPE
Modify URC Uninstructed Factor to apply tighter tolerance