## ERCOT Operations Report

## ROS & OWG

## July 2005

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 7/1/2005 3:49 | 60.115 | 34650 | 229 | -18 | At 03:41 430 MW of Up Regulation depleted and frequency at 59.926. A QSE with a -600 MW SCE at 03:41 corrected to zero and frequency overshot at 03:49 |
| 7/1/2005 12:55 | 60.101 | 51601 | -878 | -195 | 1220 (350) Out of Down Regulation for ~ 15 minutes. VDI issued to reduce generation. |
| 7/2/2005 2:07 | 60.107 | 34229 | -588 | 300 | -900(-400) VDI issued to reduce generation |
| 7/2/2005 13:05 | 60.110 | 47607 | -465 | -159 | VDI issued to reduce generation. ERCOT SCE 12:32 - 12:52 between -800 and -1150 |
| 7/2/2005 15:12 | 59.888 | 51594 | 710 | -1111 | QSE with -805 SCE |
| 7/4/2005 0:25 | 60.109 | 40387 | -1109 | -58 | -1640 (-270) Frequency low (59.95 - 59.92) for most of the previous interval and Up Regulation exhausted. Frequency recovered rapidly during the ramping period and went high as Up Regulation was recalled and Down Regulation was deployed. |
| 7/6/2005 18:06 | 60.107 | 56062 | -855 | -234 | <5% UBES, no NSRS deployed. Due to insufficient Balancing Energy consecutively requesting more UBES than available. |
| 7/19/2005 2:04 | 60.237 | 33004 | -620 | -238 | -1000 QSE SCE compensated by QSE & offset |
| 7/30/2005 22:10 | 60.101 | 41484 | -53 | -54 | -4000 (-1000) |

|  | Disturbance Data |  |
| --- | --- | --- |
| 7/2/2005 10:56 | 59.848 | 680 |
| 7/13/2005 20:33 | 59.882 | 635 run back |
| 7/29/2005 16:00 | 59.865 | 3 unit train, 695 |

At 00:50 The QSE SCE was -77 MW.  The SCE had been negative since crossing 00:00 and following the output of their fleet.  Beginning at 0:58, QSE had 900 MW of total generation and began ramping these units off line.  The decrease of the units output did not follow a normal ramping period and all units were off line by 00:28.  QSE SCE at this time was -1000. ERCOT depleted Up Regulation at 01:20.  A 575 MW Up balancing Deployment was issued for IE 2:00 and a 1450 MW Up Balancing deployment was issued for IE 02:15.  The 1000 MW was covered at 02:00 and QSE SCE ramped to zero.  The QSE was contacted and stated that they would ramp out the SCE at the top of the hour.  ERCOT understood this to mean the QSE would correct the SCE through ramping of generation.  In an effort to restore Regulation and frequency, additional Up Balancing was deployed.  With both the QSE schedule change and ERCOT deployment of Balancing to address the -1000 SCE, system frequency reached 60.237 at 02:04.  A 530 MW unit then began to run back and tripped when frequency declined to  60 Hz at 02:15.

Deployed Responsive (26) (Reported Above)

| 7/1/05 10:05 AM | 7/6/05 11:47 AM | 7/8/05 10:00 PM |  |
| --- | --- | --- | --- |
| 7/1/05 11:19 AM | 7/6/05 8:47 PM | 7/10/05 10:00 PM | 7/21/05 2:11 PM |
| 7/1/05 9:58 PM | 7/6/05 9:56 PM | 7/13/05 8:33 PM | 7/22/05 12:01 AM |
| 7/2/05 1:02 AM | 7/7/05 9:58 PM | 7/17/05 11:58 PM | 7/29/05 12:50 AM |
| 7/2/05 8:01 AM | 7/7/05 10:44 PM | 7/18/05 10:06 AM | 7/29/05 4:00 PM |
| 7/2/05 10:56 AM | 7/7/05 11:33 PM | 7/19/05 9:01 AM | 7/30/05 11:58 PM |
| 7/2/05 3:04 PM | 7/8/05 3:40 AM | 7/20/05 10:48 PM |  |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | July 04 | June 05 | July 05 |
| --- | --- | --- | --- |
| DFW | 324 | 84 | 76 |
| E RIO | 108 | 90 | 98 |
| W RIO | 59 | 34 | 31 |
| Laredo | 91 | 90 | 93 |
| Bryan Area | 0 | 32 | 71 |
| Corpus | 31 | 29 | 32 |
| Abilene | 31 | 0 | 0 |
| San Angelo | 31 | 0 | 0 |
| Western | 6 | 24 | 24 |
| Houston | 2 | 15 | 1 |
| Austin | 0 | 0 | 3 |
|  | 612 | 398 | 429 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Days of Zonal Congestion |
| --- |
| South to Houston | 14 |
| South to North | 16 |
| North to Houston | 5 |
| North to West | 9 |

| Contingency | Overloaded Element | # Occurrences |
| --- | --- | --- |
| Gibbons Creek - Bryan East - Greens Prairie 138kV | Texas A&M - Dansby 138kV | 31 |
| Lytton Spring - Zorn & Austrop - Zorn 345kV | Canyon LCRA - San Marcos 138kV | 13 |
| Uvalde - Hamilton 138kV | Asherton - West Conoco | 9 |
| Somerset - Lytle 138kV | Leon Creek - Pleasanton 138kV | 6 |
| Odessa EHV-Moss 345kV | Odessa EHV-Huntsman 138kV | 5 |
| McNeil AEN - Decker Power 138kV | Decker - Sprinkle 138kV | 5 |
| Marion - Hill country - Skyline 345kV | Hays Energy - Kendall 345kV | 5 |
| Trinidad - Watermill & TriCorner 345kV | Trinidad 345/138kV | 4 |
| Sargent Rd - Watermill 345kV | Norwood Sw 345/138kV | 4 |
| Sandow - Temple 345kV | Sandow Auto 345/138kV | 4 |
| Marion - Zorn - Clear Springs 345kV | Zorn - Seguin 138kV | 4 |
| Frontera - South McAllen 138kV | North McAllen - West McAllen | 4 |
| La Palma 345kV/138kV auto | Rio Hondo - La Palma 138kV | 3 |
| Comanche Peak Units #1 and #2 | Asherton - West Conoco 138kV | 3 |
| Bates 138kV/69kV auto | North Edinburg - Moore Field 69kV | 3 |
| Temple - Sandow 345kV | Sandow 345kV/138kV auto | 2 |
| STP - Skyline & Hill Country | Blessing - Lolita 138kV | 2 |
| Lon Hill - Koch Hearns Ferry 138kV | McKenzie - Westside 138kV | 2 |
| Braunig - Elmendorf 138kV | Leon Creek -Pleasanton 138kV | 2 |
| Austrop-Sandow 345kV | Gideon - Butler 138kV | 2 |
| VH Braunig - Elmendorf 138kV | Leon Creek - Pleasanton 138kV |
| Temple - Lake Creek & Tradinghouse 345kV | Lake Creek-Temple Switch 138kV |
| Summerset - Lytle 138kV | Leon Creek-Howard Rd 138kV line |
| Silas Ray - Military Highway 69kV | Airport 138kV/69kV Auto |
| Salem LCRA - Highway 36 138kV | Gayhill-Sandyhill 138kV |
| Rio Hondo-345kV xmfr | La Palma-Rio Hondo 138kV |
| Pharr - Pharr MVEC 138kV | W. McAllen - N. McAllen 138kV |
| Pawnee - Calaveras 345kV | Leon Crk-Pleasanton 138kV |
| Odessa EHV Switch 345kV/138kV auto #2 | Odessa EHV Switch 345kV/138kV |
| North Edinburg - Bates 138kV | North Edinburg - Moore Field 69kV |
| Marion - Zorn & Clear Spring 345kV | Comfort - Kendall 138kV |
| Marion - Zorn & Clear Spring 345kV | Hays-Kendall 345kV |
| Marion - Zorn & Clear Spring 345kV | Seguin 138kV/69kV auto |
| Marion - Skyline & Skyline - STP 345kV | Marion - Hill Country 345kV |
| Marion - Clear Springs 345kV | McCarty - Henna 138kV |
| Lytton Spring - Zorn & Austrop - Zorn 345kV | Canyon LCRA - Rohr 138kV |
| STP - Skyline & Hill Country | Blessing - Lolita 138kV |
| Lolita - Blessing 138kV | Blessing - Palacios 69kV |
| Gibbons Ck-Twin Oaks 345kV | Jewett -Watson Chapel 138kV |
| Frontera - South McAllen 138kV | Frontera - North McAllen |
| Elgin-Gilleland 138kV | Taylor-Taylor West 138kV |
| Centerville-Forney Switch 345kV | Forney Switch-Lake Hubbard 138kV |
| Bates 138kV/69kV auto | Bates-North Edinburg 69kV |
| Bates 138kV/69kV auto | Bates - Palmhurst 69kV |
| Austrop - Lost Pines 345kV | Winchester -Fayetteville 138kV |
| Asherton 138kV/69kV auto | Uvalde 138kV/69kV auto |

New RAP/SPS

2 conditional RAP posted in July and will become active when anticipated system configuration changes occur under high loading conditions.  Both RAP affect the flows on the Northeast to North interface.

New Procedures/ Forms/Operations Bulletins

| Date | Power Operations Bulletin | Subject |
| --- | --- | --- |
| 07/22/2005 | Operations Bulletin 194 | Special Protection Schemes |
| 07/05/2005 | Operations Bulletin 193 | Procurement of Additional RRS. |
| 07/05/2005 | Operations Bulletin 192 | Notification to MP’s when a critical problem exists and when it is resolved. |
| 07/01/2005 | Operations Bulletin 191 | Summary of Steady State Voltage Control |

# Security Alert Stage/ Threatcon/ Related issues

None/Yellow

Blackout/Load Shed incidences and major system voltage problems

7/1 15:13	Sandow – Temple – Killeen 345 kV lines and Killeen 345/138 kV tr tripped. The over current relay on the transformer actuated.  No CB exists on the high side of the transformer, causing the two associated 345 kV circuits to open.  Killeen Switch Tr is rated at 471/515/672 MVA and pre disturbance flow of 400 MVA.  The voltage on the 138 kV bus at Killeen Switch dropped to .9 pu and low voltages were observed as far south as Travis county.  Significant generation in the area had been forced out of service earlier in the day.  The system configuration was changed in an attempt to return system voltages within operating limits, which isolated a portion of the transmission system.  The breakers were closed back to normal status minutes after the initial switching.  At 15:35, the Killeen 138 kV bus had dropped to .817 pu.  By 16:15, 100 MW of load was shed in the Killeen area in accordance with the posted Mitigation Plan.

7/22	12:00-12:40	10 MW load shed in Collin County following a forced outage of a 138 kV switch.

Voltage Support Service Instructions

Below are the voltage set points for stations in the Corpus Christi area.  VSS instructions were given by ERCOT on the dates shown.  The time and actual kV are taken a few intervals prior to the issuance of the VSS instructions.

|  | Voltage profile | 7/2/2005 13:30 | 7/27/2005 15:00 |
| --- | --- | --- | --- |
| Barney Davis | 144.21 | 140.37 | 138.95 |
| Corpus Christi Energy | 142.83 | 139.5 | 139.4 |
| Gregory | 144.21 | 143.1 | 143.9 |
| Lon Hill | 72.105 | 70.76 | 70.54 |
| Lon Hill | 144.21 | 142.5 | 142.773 |
| Nueces Bay | 142.89 | 139.99 | 139.72 |
| Ingleside | 144.21 | 141 | 140.912 |

Communication

7/13	Held IE 21:45.  RTBM did not clear in time.

7/17	Held IE 11:45.  RTBM did not solve.

Major Computer Problems, Enhancements & Fixes

None

ERCOT peak (Unofficial)

7/6	17:00 	57,450

| OCN, Alerts, Advisories and Emergency Notices |
| --- |
| 7/1 | 3:30 -09:10 | Alert | Capacity insufficiency 1400 - 1800 |
| 7/1 | 1:30 - 3:30 | OCN | Capacity insufficiency 1400 - 1800 |
| 7/1 | 12:53-22:45 | Transmission Alert | Loss of S McAllen tr loads La Palma - Rangerville |
| 7/1 | 14:00-22:45 | Transmission Alert | Loss of Menard tr loads Ballinger - Paint Rock |
| 7/1 | 12:23-22:45 | Transmission Alert | Loss of San Miguel tr loads Derby - Pearsall |
| 7/2 | 12:40-22:30 | Transmission Alert | Loss of S McAllen tr loads La Palma - Rangerville |
| 7/2 | 17:15-20:00 | Transmission Alert | Low voltages in the Marble Falls Area |
| 7/2 | 08:55-24:00 | Transmission Alert | Loss of Menard tr loads Ballinger - Paint Rock |
| 7/2 | 13:06-22:30 | Transmission Alert | Loss of San Miguel tr loads Bigfoot tr |
| 7/3 | 15:28-23:00 | Transmission Alert | Loss of Eagle Pass - Hamilton loads Asherton - W Conoco |
| 7/3 | 05:11-23:00 | Transmission Alert | Loss of Menard tr loads Ballinger - Paint Rock |
| 7/3 | 13:30-21:30 | Transmission Alert | Loss of San Miguel tr loads Pleasanton tr |
| 7/6 | 18:00-21:31 | Transmission Alert | Loss of Frontera-S McAllen loads N McAllen - W McAllen |
| 7/7 | 06:40 - 12:05 | OCN | Capacity insufficiency IE 1700 |
| 7/7 | 11:00 - 12:00 | Transmission Alert | Loss of Marion tr loads Sequin tr |
| 7/7 | 02:36 - 12:00 | Transmission Alert | Loss of Zorn-Seguin loads Sequin - McQueeny |
| 7/10 | 22:55 | Alert | Capacity insufficiency 1500 - 1900 for operating day 7/11 |
| 7/10 | 20:35 - 22:35 | OCN | Capacity insufficiency 1500 - 1900 for operating day 7/11 |
| 7/11 | 00:00 - 03:25 | Alert | Capacity insufficiency 1500 - 1900 |
| 7/11 | 07:15 - 14:30 | Alert | Capacity insufficiency 1700 - 1800 |
| 7/11 | 15:15 - 22:45 | Transmission Alert | Loss of Gibbons Creek - Twin Oak loads Gibbons Creek - Bryan Greens Prairie |
| 7/11 | 13:15 - 22:45 | Transmission Alert | Loss of Menard tr loads Fort Mason - Mason |
| 7/11 | 11:45 - 22:45 | Transmission Alert | Loss of San Miguel tr loads Pleasanton tr |
| 7/12 | 12:15 -20:30 | Transmission Alert | Loss of Gibbons Creek - Twin Oak loads Gibbons Creek - Bryan Greens Prairie |
| 7/12 | 11:15 -20:30 | Transmission Alert | Loss of Menard tr loads Fort Mason - Mason |
| 7/12 | 11:15 - 23:30 | Transmission Alert | Loss of San Miguel tr loads Derby - Pearsall |
| 7/12 | 16:30 -20:30 | Transmission Alert | Loss of Somerset - Lytle loads Leon Creek - Pleasanton |
| 7/13 | 14:30 - 21:00 | Transmission Alert | Loss of Gibbons Creek - Twin Oak loads Gibbons Creek - Bryan Greens Prairie |
| 7/13 | 10:45 - 21:00 | Transmission Alert | Loss of Menard tr loads Fort Mason - Mason |
| 7/13 | 10:45 - 23:45 | Transmission Alert | Loss of San Miguel tr loads Derby - Pearsall |
| 7/13 | 14:30 - 23:45 | Transmission Alert | Loss of Somerset - Lytle loads Leon Creek - Pleasanton |
| 7/14 | 14:15 -20:00 | Transmission Alert | Loss of Cico - Helotes loads Kendall Tr |
| 7/14 | 14:15 -20:00 | Transmission Alert | Loss of Gibbons Creek - Twin Oak loads Gibbons Creek - Bryan Greens Prairie |
| 7/14 | 12:00 -20:00 | Transmission Alert | Loss of Menard tr loads Fort Mason - Mason |
| 7/14 | 12:00 -22:30 | Transmission Alert | Loss of San Miguel tr loads Derby - Pearsall |
| 7/14 | 14:15 -20:00 | Transmission Alert | Loss of Somerset - Lytle loads Leon Creek - Pleasanton |
| 7/18 | 7/20 | OCN | Hurricane Emily in Gulf of Mexico |
| 7/21 | 13:30 | Transmission Alert | Loss of Sandow - Temple loads Sandow tr |
| 7/22 | 0:00 - 00:31 | Transmission Alert | Loss of Sandow - Temple loads Sandow tr |
| 7/29 | 10:45 - 14:00 | Alert | Capacity insufficiency 1600 - 1700. |
| 7/29 | 09:00 - 10:45 | OCN | Capacity insufficiency 1500 - 1800. |
| 7/30 | 05:20 - 15:00 | Alert | Capacity insufficiency 16:00 - 19:00. |
| 7/30 | 3:45 - 05:20 | OCN | Capacity insufficiency 1600 - 1900. |
| 7/30 | 16:00 - 19:15 | Transmission Alert | Loss of Lon Hill - Koch Hearns Ferry loads McKenzie - Westside |