## Slide 1
Transmission Services Report: North and West RPG Projects
Bill Bojorquez
TAC
July 7, 2005

## Slide 2
DFW Recent Improvements (2004/2005)
2 – 345 kV Circuits
14 – 138 kV Circuits
2 – 345/138 kV Autotransformers
1 – new 138kV Substation
9 – Reactive Capacitors Projects
2 – 138/69 kV Autotransformers

## Slide 3
DFW Improvements Completed
Based upon May 2005 TPIT submissions
from transmission owners

## Slide 4
2006 DFW Congestion Relief Study Results

## Slide 5
Study Introduction
Initial study meeting of North RPG in April 2004
Scope included 2006 & 2008 Congestion Relief Studies
2008 was separated from first study at November 16, 2004 North RPG meeting with group consensus

## Slide 6: Process Overview
Preformed AC contingency analysis on 2006 power flow case with an economic dispatch to identify overloads.
Stakeholders proposed projects to resolve overloads.
Determined subset of projects that were needed to meet reliability needs.
  When multiple projects resolved the same reliability need then economic analysis was done to select the preferred project.
New base case was created for economic studies which includes reliability projects.
Economic analysis was performed on remaining projects to identify those with net economic benefit.
Notes: 2. Subset of projects that were needed to resolve insecure energy. These projects are deemed reliability projects.

## Slide 7
Reliability Project Improvements Added to Case for Economic Evaluation

## Slide 8: Recommended Projects
Reliability Projects
Liggett Series Reactor
Royse – Terrell Switch 69-kV Line Rebuild
Allen Switch - Plano Alma 138-kV Terminal Equipment Upgrade
E. Levee – Reagan Street 138-kV Line Rebuild
Reliability Projects That Provide Additional Economic Benefits
Plano Tennyson 345/138-kV Autotransformer Installation ($4.0 M)
Economic Projects Cost
Centerville Switch – Parkdale 138-kV Line Rebuild $9.8 M
Ben Davis – Royse 345-kV Line Upgrade (TMPA) $4.5 M
Johnson Switch – Venus 345-kV Line Upgrade $4.0 M
DeCordova Everman 345-kV Line Upgrade $8.2 M
TOTAL $30.5 M
Annual Benefit (2006) $19.3 M

## Slide 9
Reliability Projects
Reliability/Economic Projects
Economic Projects

## Slide 10
Reliability Projects
Reliability/Economic Projects
Economic Projects

## Slide 11: Other Recommendations
TXU ED should install breakers at the Decordova bus on the Decordova to Everman 345-kV circuit and at the Benbrook bus on the Benbrook to Sycamore Creek 345-kV circuit , if feasible
Perform follow up study to determine additional upgrades with longer lead times that would be economic to reduce the impact of congestion

## Slide 12: DFW/North Zone 2009 Congestion Relief Study
Goal is to identify longer lead time reliability-driven and economic projects for DFW and surrounding area throughout planning horizon
Process Overview:
  Develop a Preliminary Study Case
  Identify reliability problems in Study Case
  Identify reliability projects and develop a Economic Base Case
  Identify congestion problems for various generation scenarios, based on this case
  Identify projects to alleviate identified congestion
  Analyze economics of proposed projects
  Include the economic projects in the case and iterate steps 4 - 7
  Make recommendation
Study will be complete in 6-8 months

## Slide 13
McCamey Area Study Results

## Slide 14
McCamey Area Study Results
May 2003, the ERCOT BOD approved two 345 kV transmission projects contingent upon IAs totaling 1500 MW and 2000 MW in McCamey
Nov 2004, ERCOT Staff completed examination of the transfer capability out of the McCamey area
  Indicated significant 138 kV additions substantially improve transfer capability
  Showed voltage control and thermal overload issues above 600 MW transfer level
  Recommended reconsideration and acceleration of 345 kV transmission projects

## Slide 15
McCamey Area Study Results
Jan 2005 (West RPG Meeting), AEP presented reactive plan and temperature adjusted line ratings
ERCOT Staff reexamined application of reactive plan and adjusted ratings
  Staff concluded 755 MW (total McCamey generation) can be exported from the McCamey area
  Assumes full implementation of plan and adjusted ratings
ERCOT Staff and TSP’s will continue to review the need for 345 kV lines as additional generators request interconnection in McCamey

## Slide 16
Questions
?
?