## Slide 1: ERCOT CPS1 by Day – Aug 2005

## Slide 2: ERCOT CPS1 by Interval – Aug 2005

## Slide 3: ERCOT 12 Month Rolling AVG CPS1
124.89 CPS1

## Slide 4: Daily RMS1
2000 ------2001-------
2002-------2003-------
2004-------2005---
Notes: 2000 data Jan 1 through July 31 and one week in October. 2004. Remaining 2000 data is still being assembled. The raw 2 second data was in a different format from the Jan-July data.
All data for 2004 and Jan-Aug 2005 data was included.

## Slide 5: 2004-2005 Summary

## Slide 6: 2004-2005 Xbar-R Charts
Weekly process control charts are above for 2004-2005. The top graph is average weekly RMS1 (those above the UCL of 29.3mHz would be of most concern). The bottom chart is intra-week variation. Looks to me like there was an unusual day in the 74th week (looks to be an usually quite day on May 30, 2005).
Notes: This data does not include August 2005.

## Slide 7: Daily RMS1 2004-2005
The graph above is a daily process control chart for 2004-2005. Days noisier than 32 mHz would merit some closer review to identify the underlying control/process problems.

## Slide 8: Daily RMS1 2000
The graph above is daily performance for 2000. Prior to our market, a day with over 21mHz noise would be unusual.
Notes: August thru December 2 second data was in a different format. A program has been written to convert it to 1 minute average data to include in this analysis. This graph will be updated as soon as this process is complete.

## Slide 9: Regression Analysis
A regression analysis implies typical daily RMS1 is 26mHz, but was 9.5mHz lower pre-market (more precisely in 2000). It is 1 mHz lower in summer and winter.
Regression Analysis: Daily Epsilon 1 versus Premarket, summer, Winter
The regression equation is Daily Epsilon 1 (RMS1) = 0.0262
-0.00951 Premarket
-0.00144 Summer
-0.00120 Winter

## Slide 10
Predictor Coef SE Coef T P
Constant 0.0262442 0.0001607 163.34 0.000
Premarket -0.0095144 0.0002288 -41.59 0.000
summer -0.0014439 0.0002471 -5.84 0.000
Winter -0.0011975 0.0002486 -4.82 0.000
S = 0.00287804 R-Sq = 69.2% R-Sq(adj) = 69.1%
Analysis of Variance
Source DF SS MS F P
Regression 3 0.0147685 0.0049228 594.32 0.000
Residual Error 792 0.0065602 0.0000083
Total 795 0.0213287

## Slide 11: Root Mean Square
Root Mean Square RMS
A kind of average sometimes used in statistics and engineering, often abbreviated as RMS. To find the root mean square of a set of numbers, square all the numbers in the set and then find the arithmetic mean of the squares. Take the square root of the result. This is the root mean square.
or

## Slide 12: Mean
Mean
Another word for average. Mean almost always refers to arithmetic mean. In certain contexts, however, it could refer to the geometric mean, harmonic mean, or root mean square.

## Slide 13: XbarR chart
An XbarR chart is a specific member of a family of control charts. A control chart is a tool used in quality control, specifically SPC or statistical process control.
A control chart is a plot of measurements of a product on two special scales, usually located above and below each other and running horizontally. For the specific case of the XbarR chart, the top chart has a centerline represented by Xbar, which is simply the sample average. The top and bottom borders are also known as the upper control limit or UCL and the lower control limit or LCL, which are represented by plus and minus three standard deviations from the mean. The bottom chart has the range of each subgroup plotted in a similar manner. The significance of subgroups is explained below.
The purpose of any control chart is to help determine if variations in measurements of a product are caused by small, normal variations that cannot be acted upon, or by some larger special cause that can be acted upon or fixed. The type of chart to be used is based on the nature of the data.
The XbarR chart is normally used for numerical data that is grouped in subgroups in some logical manner, for example 3 games of bowling that occur on one night. This allows the night to be considered as a unit, so a special cause such as a slippery floor or a sick bowler will be more obvious as a point on the chart.

## Slide 14: Skewness
In probability theory and statistics, skewness is a measure of the asymmetry of the probability distribution of a real-valued random variable. Roughly speaking, a distribution has positive skew (right-skewed) if the higher tail is longer and negative skew (left-skewed) if the lower tail is longer (confusing the two is a common error).
Skewness, the third standardized moment is written as γ1 and defined as
where μ3 is the third moment about the mean and σ is the standarddeviation. Equivalently, skewness can be defined as the ratio of the third cumulant κ3 and the third power of the square root of the second cumulant κ2:

## Slide 15: Special Thanks
Thanks to Ananth Palani with The City of Garland for converting the year 2000 two second frequency data into one minute averages.
Thanks to Terry Bilke with MISO for the statistical analysis