## ERCOT Operations Report

## ROS & OWG

## July 2005

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 8/2 19:03 | 60.102 | 53769 | -712 | 336 | 250 MW drop in steel mill load |
| 8/7 0:09 | 60.103 | 35821 | 65 | 50 | -1940 (-375) |
| 8/10 0:10 | 60.104 | 34868 | -279 | 372 | -950 (-325) |
| 8/10 6:06 | 59.899 | 33219 | 271 | -591 | 2480 (710) |
| 8/11 18:37 | 60.142 | 52017 | -809 | -648 | See below graph |
| 8/24 22:07 | 60.101 | 49242 | -459 | 264 | -6200 (-1230) |
| 8/25 1:36 | 60.111 | 36769 | -87 | 613 | Individual QSE SCE with +400 SCE 00:00 - 02:00. |
| 8/27 17:32 | 60.122 | 55189 | -386 | -19 | When NSRS is recalled before the original end time, deployments are correct but SPD calculation doesn't account for change and considers recalled NSRS as still deployed. Procedures on deploying NSRS have been updated and an SCR was submitted to correct this. |

|  | Disturbance Data |  |
| --- | --- | --- |
| 8/5 19:28 | 59.883 | 490 |
| 8/18 7:35 | 59.883 | 345 |
| 8/22 8:00 | 59.884 | 555 |

Deployed Responsive (13) (Reported Above)

| 8/5/05 19:28:42 | 8/10/05 6:06:08 | 8/19/05 23:04:32 |
| --- | --- | --- |
| 8/6/05 9:09:36 | 8/14/05 20:22:18 | 8/22/05 6:08:52 |
| 8/8/05 18:50:38 | 8/15/05 6:04:44 | 8/22/05 8:00:20 |
| 8/8/05 20:29:34 | 8/18/05 7:35:06 | 8/25/05 2:48:20 |
|  | 8/19/05 17:04:40 |  |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | August 04 | July 05 | August 05 |
| --- | --- | --- | --- |
| DFW | 305 | 76 | 75 |
| E RIO | 107 | 98 | 101 |
| W RIO | 54 | 31 | 28 |
| Laredo | 93 | 93 | 93 |
| Bryan Area | 18 | 71 | 93 |
| Corpus | 31 | 32 | 33 |
| Northeast | 0 | 0 | 18 |
| North | 0 | 0 | 8 |
| Western | 0 | 24 | 21 |
| Houston | 0 | 1 | 9 |
| Austin | 0 | 3 | 0 |
|  | 786 | 429 | 479 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overloaded Element | Days |
| --- | --- | --- |
| Gibbons Creek - Bryan East - Greens Prairie 138kV | Texas A&M - Dansby 138kV | 28 |
| Marion - Hill Country & Skyline 345kV | Schertz - Parkway LCRA 138kV | 21 |
| La Palma 345/138kV auto | La Palma - Rio Hondo 138kV | 8 |
| Lytton Springs - Zorn & Austrop - Zorn 345kV | Canyon LCRA - San Marcos 138kV | 8 |
| Lytton Springs - Zorn & Austrop - Zorn 345kV | Canyon - Rohr 138kV | 7 |
| Odessa 345/138kV 2H | Odessa 345/138kV 1H | 6 |
| North Denton 138/69kV T1 auto | North Sanger - Spring | 6 |
| Greenville Steam T1 138/69kV #1 | Greenville Steam 138/69kV #2 | 5 |
| Frontera - South McAllen 138kV | North McAllen -West McAllen 138kV | 6 |
| Hill Country - Marion & STP 345kV | Marion - Skyline 345kV | 4 |
| Sandow - Temple 345kV | Sandow 345kV auto | 3 |
| Kendal 58AT2 345/138kV auto | Comfort - Raymond Baker 138kV | 3 |
| Loss of Comanche Peak Units 1-2 | Asherton - West Conoco 138kV | 3 |
| Marion - Zorn & Clear Springs 345kV | Zorn AT1 345/138kV Auto | 2 |
| Marion - Zorn & Clear Springs 345kV | Seguin - Zorn 138kV | 2 |
| Sargent Rd. - Watermill SW 345kV | Oak Cliff South - Cedar Crest | 2 |
| Lytle - Summerset 138kV | Leon Creek - Pleasanton 138kV | 2 |
| La Palma - Rio Hondo 345kV | La Palma - Rio Hondo 138kV | 2 |
| North Denton 138/69kV T1 auto | Denton T1 Auto | 2 |
| Bates 138/69kV auto | Bates - Palm Hurst 69kV | 2 |
| West Levee 345/138 #1 | West Levee 345/138 #2 | 1 |
| Fern St. - Ballpark 138kV | Tuttle - Austin Road 138kV | 1 |
| Temple Lake CK & Tradinghouse 345 | Temple SW-Lake Creek SES 138 | 1 |
| Oklaunion G1 | Stephenville-Lingleville 138kV | 1 |
| Denton 138/69kV T1 auto | Spencer - Denton Steam 69kV | 1 |
| Rio Hondo - La Palma 345kV | Rio Hondo - La Palma 138kV | 1 |
| Midland East - Odessa EHV 345kV | Odessa EHV 345/138kV Auto | 1 |
| Bates 138/69kV auto | North Edinburg - Moore Field 69kV | 1 |
| Mt. Enterprise - Trinadad & Martin Lake 345kV | Nacogdoches Auto | 1 |
| Morgan Creek 345/138kV #1 auto | Morgan Creek 345/138kV auto #2 | 1 |
| Sargent Road - Watermill 345kV | Mesquite East -Mesquite West 138kV | 1 |
| South McAllen 138/69kV Auto | La Palma - Rangerville 69kV | 1 |
| Marion - Hill Country - Skyline 345kV | Kendal -Comfort 138kV | 1 |
| Norwood SW - Liggett SW & Cedar Hill SW | Irving Hunter Ferrell - Norwood SW | 1 |
| Austrop - Sandow 345kV | Gideon - Butler LCRA 138kV | 1 |
| Centerville Road - Forney SW 345kV | Forney Sw - Duck Creek Tap 138kV | 1 |
| Royse SW - Ben Davis 345kV | Forney Sw - Duck Creek Tap 138kV | 1 |
| CPSES - Decordova/Wolf Hollow - Rocky Creek | Concord 345/138kV auto | 1 |
| STP - Dow 345kV | Blessing - Lane City 138kV | 1 |
| Trinidad - Stryker Creek & Trindad - Mt. Enterprise | Athens Tap - Athens SW 138kV | 1 |

New RAP

8/10	Forney – Centerville Sw 345 kV

8/19	Odessa Tr 2

- 8/25	Copperas Cove LCRA – Lampasas LCRA 138 kV Single Circuit

- 8/25	Forest Grove – Trinidad 138 kV Single Circuit (Forest Grove – Mabank Tap)

New Procedures/ Forms/Operations Bulletins

| Date | Power Operations Bulletin | Subject |
| --- | --- | --- |
| 08/29/2005 | ERCOT POB 207 | OOME Respond to H/A Results |
| 08/29/2005 | ERCOT POB 206 | T& S Desk – OOME/ VDI Guidelines |
| 08/15/2005 | ERCOT POB 205 | T & S Desk - VDI for Okla TCN |
| 08/10/2005 | ERCOT POB 203 | Shift Supervisor Desk - V3R20 |
| 08/09/2005 | ERCOT POB 202 | Frequency Desk – Unsched Gen |
| 08/09/2005 | ERCOT POB 201 | Shift Sup Desk - Unit Testing. |
| 08/05/2005 | ERCOT POB 200 | DFW Dynamic Reactive Reserves |
| 08/02/2005 | ERCOT POB 199 | T & S Desk V3R52 |
| 08/02/2005 | ERCOT POB 198 | Frequency Control Desk - V3R28 |
| 08/02/2005 | ERCOT POB 197 | Operating Period Desk - V2R10 |
| 08/02/2005 | ERCOT POB 196 | Day Ahead Desk - V3R19 |
| 08/02/2005 | ERCOT POB 195 | Changes to the SPS Procedure. |

Blackout/Load Shed incidences and major system voltage problems

8/10  	39 MW of load shed in Cameron County following the loss of a 345 kV line and transformer.  20 MW total at two stations was shed from 16:36 to 17:15.  An additional 19 MW was shed at 3 different stations from 17:08 to 17:22

8/25	07:53 Three 138 kV circuits tripped out of service.  Service to South Padre Island was disrupted.  All customers restored by 08:28.

8/29	9 MW of load lost in Schliecher County.  A bus cleared following a PT failure.

Voltage Support Service will be presented separately.

Major Computer Problems, Enhancements & Fixes

ERCOT system bias will be adjusted on 9/30 from 520.5 MW/.1 Hz to 489 MW/.1Hz.

Communication

8/11	Held 17:45 interval

8/29	Held 01:30 interval

8/29     Held 23:30 interval

ERCOT peak (Unofficial)

8/23	17:00  60,279

| August Transmission Alerts |  |  |  |
| --- | --- | --- | --- |
| Day | Time | Contingency | Monitored Element |
| 1-Aug | 15:17 - 15:55 | Gibbons Creek - Twin Oak Sw | Gibbons Creek - Brian Greens Prairie |
| 1-Aug | 14:31-19:30 | Tyler W Elkton | Tyler NW transformer |
| 2-Aug | 13:55 - 19:00 | Tyler W Elkton | Tyler NW transformer |
| 3-Aug | 16:45 - 18:30 | S McAllen transformer | La Palma - Rangerville |
| 3-Aug | 14:55 - 18:30 | Kendal transformer | Comfort - Raymond Barker |
| 3-Aug | 14:48 - 18:30 | Tyler W Elkton | Tyler NW transformer |
| 4-Aug | 13:52 - 15:45 | Tyler W Elkton | Tyler NW transformer |
| 5-Aug | 09:45 - 11:23 | Harlingen Sw transformer | Ramondville transformer |
| 7-Aug | 14:45 - 19:00 | San Miguel transformer | Derby - Pearsall |
| 8-Aug | 16:15 - 17:30 | Asherton transformer | Uvalde - La Pryor |
| 8-Aug | 20:30 - 22:30 | Greenville Steam transformer 1 | Greenville Steam transformer 2 |
| 8-Aug | 16:09 - 19:50 | Harlingen Sw transformer | La Palma - San Benito |
| 8-Aug | 15:39 - 19:50 | La Palma transformer | La Palma - Rio Hondo |
| 8-Aug | 15:36 - 17:30 | Lon Hill transformer 1 | Lon Hill transformer 2 |
| 8-Aug | 15:05 - 19:50 | San Miguel transformer | Derby - Pearsall |
| 8-Aug | 15:37 - 19:50 | S McAllen transformer | La Palma - Rangerville |
| 8-Aug | 15:41 - 19:50 | S McAllen - Frontera | N McAllen - W McAllen |
| 8-Aug | 15:57 - 17:30 | Laredo transformer 1 | Laredo transformer 2 |
| 9-Aug | 14:25-19:00 | Eagle Pass - Hamilton | Asherton - W Conoco |
| 9-Aug | 15:14-20:30 | Harlingen Sw transformer | La Palma - San Benito |
| 9-Aug | 15:11-19:00 | La Palma transformer | La Palma - Rio Hondo |
| 9-Aug | 12:43-20:30 | San Miguel transformer | Derby - Pearsall |
| 9-Aug | 12:52-19:00 | San Miguel - Sigmour | Kennedy Sw - Kennedy |
| 9-Aug | 11:49-19:00 | S McAllen transformer | La Palma - Rangerville |
| 10-Aug | 14:13-21:00 | Harlingen Sw transformer | La Palma - San Benito |
| 10-Aug | 14:15-0:00 | La Palma transformer | La Palma - Rio Hondo |
| 10-Aug | 14:16-21:00 | S McAllen transformer | La Palma - Rangerville |
| 11-Aug | 10:39-12:55 | La Palma unit | Rio Hondo – La Palma |
| 11-Aug | 10:39-12:55 | Rio Hondo transformer | Magic Valley – Hidelburg |
| 11-Aug | 15:04-19:30 | La Palma transformer | La Palma - Rio Hondo |
| 11-Aug | 15:05-19:30 | San Miguel transformer | Derby - Pearsall |
| 11-Aug | 12:45-19:30 | S McAllen transformer | La Palma - Rangerville |
| 12-Aug | 06:15-11:15 | Greenville Steam transformer 1 | Greenville Steam transformer 2 |
| 12-Aug | 07:55-11:55 | Calaveras – Skyline/Walzem Rd | Westside - Fivepoints |
| 12-Aug | 11:56-21:35 | Buda - Turnersville | Paleface – Johnson City |
| 12-Aug | 14:32-19:29 | San Miguel transformer | Derby - Pearsall |
| 12-Aug | 12:37-21:35 | S McAllen transformer | La Palma - Rangerville |
| 12-Aug | 16:40-19:30 | Gibbons Creek transformer | Gibbons Creek transformer |
| 12-Aug | 16:15-21:35 | Graham - Rice | Oran (TU) - Oran (TMPP) |
| 13-Aug | 13:30 - 23:30 | Bates transformer | N Edinburg - Moore Field |
| 14-Aug | 12:45 - 23:00 | Bates transformer | N Edinburg - Moore Field |
| 16-Aug | 15:20 - 19:00 | La Palma transformer | La Palma - Rio Hondo |
| 16-Aug | 17:45 - 19:00 | San Miguel transformer | Derby - Pearsall |
| 17-Aug | 20:00 - 21:15 | Anna SW transformer 2 | Anna SW transformer 1 |
| 17-Aug | 11:21 - 13:19 | Oklaunion transformer | Lake Wichita Sw - Holiday |
| 18-Aug | 16:26 - 20:15 | Eagle Pass - Hamilton | Asherton - W Conoco |
| 18-Aug | 14:55 - 20:15 | Gibbons Creek transformer 1 & 3 | Gibbons Creek transformer 2 |
| 22-Aug | 15:00 - 15:45 |  | Asherton - W Conoco |
| 22-Aug | 13:45 - 22:40 |  | Derby - Pearsall |
| 23-Aug | 13:15 - 22:30 | San Miguel transformer | Derby - Pearsall |
| 24-Aug | 16:00 - 21:15 | Lewisville Sw transformer | Carrollton NW - Lakepoint |
| 24-Aug | 13:00 - 22:30 | San Miguel transformer | Derby - Pearsall |
| 25-Aug | 11:45 - 12:45 | Military Highway - La Palma | La Palma - Cavazos |
| 25-Aug | 12:45 - 23:45 | San Miguel transformer | Derby - Pearsall |
| 27-Aug | 10:15 -17:57 | Rio Pecos Tr | Voltage violations |
| 27-Aug | 17:36-22:10 | Marion - Hill Country/Skyline | Schertz - Parkway |
| 27-Aug | 17:33-22:10 | San Miguel transformer | Derby - Pearsall |
| 27-Aug | 17:45-19:44 | Walnut Springs transformer | Olsen - Sycamore |
| 28-Aug | 13:00 -21:41 | San Miguel transformer | Derby - Pearsall |
| 29-Aug | 16:15 - 22:15 | Kingsville - Alice | Falfurrias transformer |
| 29-Aug | 11:45 - 22:15 | San Miguel transformer | Derby - Pearsall |
| 29-Aug | 11:15 - 22:15 | Sonora transformer | voltage violations |
| 30-Aug | 13:00 -22:30 | Gibbons Creek transformer 1 & 3 | Gibbons Creek transformer 2 |
| 30-Aug | 13:00 -22:30 | Kingsville - Alice | Falfurrias transformer |
| 30-Aug | 13:00 -22:30 | San Miguel transformer | Derby - Pearsall |
| 31-Aug | 16:00 - 21:00 | Bates - Garza | voltage violations |
| 31-Aug | 12:00 - 22:00 | Flatonia transformer | Yoakum transformer |
| 31-Aug | 13:00 - 23:30 | Gibbons Creek transformer 1 & 3 | Gibbons Creek transformer 2 |
| 31-Aug | 13:00 - 22:00 | Kingsville - Alice | Falfurrias transformer |
| 31-Aug | 16:00 - 21:00 | La Palma transformer | La Palma - Rio Hondo |
| 31-Aug | 12:00 - 22:00 | San Miguel transformer | Derby - Pearsall |
| 31-Aug | 18:15 - 21:00 | Walnut Springs transformer | Olsen - Sycamore |
| 31-Aug | 15:45 - 21:00 |  | Sandow transformer |

8/8	MPs have been approved for the Lon Hill and Laredo Auto Alerts.

| Other OCN, Alert & Emergency Notice |  |  |
| --- | --- | --- |
| 01-Aug-05 | 8:13 - 10:12 | OCN - Capacity deficit hours 15:00 - 18:00 |
| 02-Aug-05 | 03:30 - 4:30 | Alert - Capacity deficit hours 16:00 - 17:00 |
| 02-Aug-05 | 00:55 - 03:30 | OCN - Capacity deficit hours 16:00 - 18:00 |
| 03-Aug-05 | 03:40 - 18:00 | Alert - Capacity deficit hours 15:00 - 18:00 |
| 03-Aug-05 | 02:00 - 03:40 | OCN - Capacity deficit hours 15:00 - 18:00 |
| 06-Aug-05 | 2:30 - 5:05 | Alert - Capacity deficit hours 16:00 - 17:00 |
| 06-Aug-05 | 09:00 - 12:15 | OCN - Capacity deficit hours 16:00 - 17:00 |
| 06-Aug-05 | 00:30 - 2:30 | OCN - Capacity deficit hours 16:00 - 18:00 |
| 10-Aug-05 | 16:52 | Emergency Notice: loss of Rio Hondo - La Palma loading Rio Hondo - La Palma. |
| 10-Aug-05 | 04:00-14:30 | OCN - Capacity deficit hours 16:00 - 18:00 |
| 11-Aug-05 | 05:00-18:30 | Alert - Capacity deficit hours 15:00 - 18:00 |
| 11-Aug-05 | 0:15-12:55 | Emergency Notice: loss of Rio Hondo - La Palma loading Rio Hondo - La Palma. |
| 11-Aug-05 | 02:50-05:00 | OCN - Capacity deficit hours 15:00 - 19:00 |
| 13-Aug-05 | 4:14 - 8:30 | Alert - Capacity deficit hours 15:00 - 18:00 |
| 13-Aug-05 | 03:00 - 4:14 | OCN - Capacity deficit hours 15:00 - 18:00 |
| 22-Aug-05 | 2:00 - 13:00 | Alert - Capacity deficit hours 16:00 - 18:00 |
| 22-Aug-05 | 01:00 - 2:00 | OCN - Capacity deficit hours 16:00 - 18:00 |
| 23-Aug-05 | 2:00 - 9:00 | Alert - Capacity deficit hours 16:00 - 17:00 |
| 23-Aug-05 | 0:15 - 2:00 | OCN - Capacity deficit hours 16:00 - 18:00 |
| 26-Aug-05 | 03:10-16:45 | Alert - Capacity deficit hours 16:00 - 17:00 |
| 26-Aug-05 | 01:15 - 03:10 | OCN - Capacity deficit hours 15:00 - 18:00 |
| 27-Aug-05 | 12:30 - 16:30 | Alert - Capacity deficit hours 16:00 - 17:00 |
| 27-Aug-05 | 11:15 -12:30 | OCN - Capacity deficit hours 16:00 - 18:00 |
| 31-Aug-05 | 4:30 - 6:15 | Alert - Capacity deficit hours 16:00 - 18:00 |
| 31-Aug-05 | 03:30 - 4:30 | OCN - Capacity deficit hours 16:00 - 18:00 |

Other information requests from August ROS

On 7/29 at 16:00 RRS service was deployed for about 30 minutes.  3 units totaling 696 MW began to trip just prior to 16:00 and were completely off line in about 1 minute 20 seconds.  Prior to the event, ERCOT SCE had been negative for some time and  -220 at the time of the trip, depleting nearly 75% of the available Up Regulation.

The SCE increased to -1500 MW.  437 MW of RRS had just been deployed and the 696 MW lost by the QSE was carried as SCE throughout the deployment of the RRS.  As QSE’s responded to the RRS deployment, the ERCOT SCE reduced to -800 MW.  RRS and Up Regulation began to ramp down at 16:11 when frequency recovered to 60 Hz for a brief time.  When frequency again declined, the RRS signal stopped recalling and held a 248 MW deployment for 8 minutes until frequency again briefly recovered to 60 Hz, when RRS and Regulation again begin to recall and then hold as frequency drops.

The amount of Regulation deployed takes into account the amount of RRS currently deployed.  If there is sufficient control in progress, Regulation will not continue to increase for low frequencies, and RRS will not begin to recall until frequency reaches an acceptable threshold.  The remaining SCE not attributed to the lost resources consisted of several QSE’s with small negative SCE.

7/30 16:00-19:15 A Transmission Alert was issued for the loss of Lon Hill – Koch Hearns Ferry loading McKenzie – Westside.  This is an uncommon occurrence and was due to a forced outage in the area.

7/7   02:42   A planned 345 kV transmission outage actuated a line tripping scheme on an underlying 138 kV line in the Northeast Zone.  The loading on the two lines prior to the outage indicate that the scheme actuated as designed.  The planned outage returned to service at 03:45 and the 138 kV line was returned to service at 03:50.

8/3  10:10 Planned fail over and fail back completed at 10:35.  Notification via hotline made at 09:48. AGC was inoperable 10:12 – 10:16.  Completion of the evolution was not communicated through a hotline call.