2006

ERCOT Methodologies for Determining Ancillary Service Requirements

Draft – For consideration of the ROS

TABLE OF CONTENTS

Executive Summary	2

Regulation Reserve (RGRS) Requirement Details	2

Non-Spinning Reserve Requirements	2

Replacement Reserve Requirements	2

Balancing Energy Requirement	2

Minimum Balancing Energy Service (BES) Down Bid Percentage Requirement	2

Responsive Reserve (RRS) Requirement	2

Responsive Reserve % LAAR	2

# Executive Summary

##### Introduction

ERCOT Protocol 6.4.1(2) requires that methodologies for determining the amounts of Ancillary Services to be required by ERCOT must be developed at least annually. Protocol 6.4.1(4) requires approval of this methodology by the ERCOT Board of Directors.

This document discusses the various Ancillary Services for which requirements are to be developed. Further, detailed methodologies for determining those requirements are attached as part of this document.

The approach taken is to summarize the details that are built into the operations systems purchased for the purpose of implementing the operations requirements of ERCOT Protocols and to provide the individual procedures that ERCOT will use for those services whose quantity requirements are not determined within the operations systems.

.

Overview of ERCOT AS Methodology

Methodologies are required for the determination of the quantities of Regulation Reserve Service (RGRS) and Non Spinning Reserve Service (NSRS) required to maintain system reliability.  Those procedures are discussed below.

The ERCOT Operating Guides establish a fixed requirement of 2300 MW of Responsive Reserve Service (RRS). This quantity will be used until it is determined that a change is appropriate. At that time, the changed methodology will be developed and presented to ERCOT TAC and the ERCOT Board for approval.

##### Regulation Reserve Requirement

ERCOT has developed a procedure for determination of the base requirement for Regulation Reserve Service. The base requirement will be calculated as follows:

Calculate the average and standard deviation for the up and down regulation service in the previous month, and for the same month of the previous year. For each of these months calculate the amount of regulation service required by hour to provide an adequate supply of regulation service capability 98.8% of the time. (2.5 Standard deviations) To facilitate market operations, ERCOT will divide these requirements into multiple hour "blocks" of constant requirements using a minimization process.

Experience has shown that, although the total amount of regulation reserve appears to be sufficient for most hours using the methodology described above, the maximum ramp rate of deployment [defined by protocols as the amount procured divided by 10] appears to be insufficient during the 0600 and 2200 time periods each day.   For this reason, ERCOT will examine these time periods each month for maximum ramp rate requirements and; if greater than the amount calculated above, will set a higher RRS requirement for these periods.

If experience indicates that these methods result in repeated shortages of regulation reserve; ERCOT may increase these requirements after issuing an OCN explaining its actions. If this option is exercised ERCOT must provide a report to TAC and the Board of Directors explaining its actions and new methodology at their next meeting.

Non-Spinning Reserve Requirements

ERCOT has developed a heuristic procedure for determining of the requirement for Non Spinning Reserve Service. The plan is described in detail in the attached sections.  In simple terms, ERCOT will plan to purchase NSRS equal to the largest unit planned to be in operation for periods of projected higher risk. This is intended to cover the exposure to loss of the largest unit and also to provide for load forecast error. ERCOT will monitor the continued need for NSRS as the RPRS market matures.

###### Replacement Reserve and Balancing Energy Requirements

The operations systems used by ERCOT develop internally, as part of the on-line real-time market operations and power operations activities, the requirements for Replacement Reserve Service and Balancing Energy Service. These quantities may vary, depending upon the parameters described in the attached descriptions.

Minimum Balancing Energy Down Requirement

The balancing energy down requirement will be determined by examining the historic needs for the past three (3) months and determining how much balancing energy down will be required for ERCOT 99.9% of the time.  The procedure for estimating this requirement is described in the attached sections.

Responsive Reserve Requirement

Responsive Reserves are resources ERCOT maintains to restore the frequency of the ERCOT System within the first few minutes of an event that causes a significant deviation from the standard frequency.  The ERCOT Operating Guides set the RRS requirement at 2300 MW for all hours under normal conditions. The Operating Guides allow ERCOT to increase that requirement under extreme conditions.

### Regulation Reserve (RGRS) Requirement Details

##### Introduction

Regulation Reserves are resources that can be deployed by ERCOT in response to changes in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.  ERCOT is required to evaluate normal requirements for Regulation Service – Up (regulation up) and Regulation Service – Down (regulation down) on an annual basis. It is ERCOT’s intent to use historical rates of regulation usage to perform this evaluation.

This normal regulation requirement may be increased by a multiple of two (2) during projected severe stress conditions such as forecasted extreme weather days.

##### Summary

To evaluate regulation requirements, ERCOT collects monthly historic deployed regulation data. These data were used to calculate average historically deployed regulation for five-minute periods. By calculating the mean and standard deviation of the amounts of deployed regulation up and deployed regulation down, ERCOT will estimate the expected needs for similar months.

By arranging for 2.5 standard deviations times the historic average usage for each hours requirement; ERCOT provides the mathematical expectation that sufficient regulation will be available 98.8% of all periods. This requirement may appear excessive until you realize that this implies that 1.2% of every month, or 35 intervals/month; ERCOT expects to exhaust available regulation services.

##### Procedure

Using archived data, ERCOT will calculate the mean and standard deviation of actual regulation deployed daily for the previous month and the same month of the previous year. Using this data ERCOT will select multiple hour periods of “similar” amounts of reserve deployment, and will, for each of these blocks, select the maximum “average” RRS deployment + 2.5 Standard deviations for the requirement for this block of hours. There will be between 4 and 6 blocks for each day, and each block may have a different number of hours.

One of the aforementioned blocks will take place around 0500--0700 hours and another will take place around 2100--2300 hours.  During these time periods, large schedule changes typically occur, related to 16 hour block energy sale products.  Because of these large energy swings, ERCOT often finds its maximum deployment rate of RRS insufficient to control frequency..  During these times; ERCOT may see the need for extra regulation to be available to cover the amount needed to respond to such large schedule changes.  The amount of regulation needed during these intervals will be calculated based on the estimated MW ramp rate required to compensate for the observed rate of change in frequency.  The conversion of frequency change to MW will be estimated as : Hz*bias, where bias is the amount of MW required in ERCOT to produce a 0.1 Hz frequency change in ERCOT.   ERCOT will convert this energy change to a ramp rate requirement for the time frame, and will estimate the regulation requirement as ten (10) times the estimated ramp rate requirement.  For the 0600 time block and 2200 time block the larger of the two requirements will be selected.

ERCOT may include historic deployment of responsive reserve as a part of regulation deployment in this analysis.

ERCOT will calculate and post this requirement by the 20th of each month for the succeeding month as required by the protocols.

ERCOT will post this requirement for each day of the month as required by the Protocols.

If historic regulation deployment information is noticeably “truncated” by historic cases of running out of regulation up or regulation down, ERCOT may adjust the regulation requirement to compensate. If such compensation is applied, ERCOT shall post a message on the Market Information System explaining the adjustment and the reason for it.

### Non-Spinning Reserve Requirements

##### Introduction

Non-Spinning Reserve Service (NSRS) consists of resources capable of being ramped to a specified output level within thirty (30) minutes or Loads acting as a Resource that are capable of being interrupted within thirty (30) minutes and that are capable of running (or being interrupted) at a specified output level for at least one (1) hour.  NSRS is used to replace loss of generating capacity or to compensate for load forecast errors on days in which large amounts of reserve are not available online.

In each case, NSRS is needed if the market does not plan to have amounts of spinning reserve available significantly in excess of energy requirements.

##### Summary

ERCOT will purchase NSRS when projected risk of insufficiency is higher than normal, or large amounts of spinning reserve are not projected to be available online based on resource plans.

Using this methodology ERCOT procures NSRS when hot weather, cold weather, or uncertain weather is expected, and when amounts of spinning reserve less than 4,600 MW (including that used for RRS) are projected.

##### Discussion

In each case, NSRS is needed if the market does not plan to have large amounts of spinning reserve available in excess of energy requirements.

Historically, the need for NSRS has occurred during hot weather, during cold weather, during unexpected changes in weather, or during large unit trips when large amounts of spinning reserve have not been on line.

Examples of circumstances when NSRS has been used are:

	Across peak hours during spring and fall months when hotter than expected weather with large amounts of capacity offline resulted in EECP events.

	Afternoons during Summer seasons when high loads and unit outages outstripped the capability of base load and normal cyclic units.

	Cold weather events when early morning load pickup outpaced the ability of generation to follow.

	Major unit trips when large amounts of spinning reserve were not online.

In each case, the need for quick start non-spinning reserve has been evident when there is not a large excess of spinning reserve on line.

This suggests a principle be used in determining NSRS requirements:

	NSRS is needed when large amounts of spinning reserve are not online.

ERCOT requires a minimum of 2300 MW of responsive reserve, so clearly this is not a “large amount”.

ERCOT believes spinning reserves of 4600 MW qualify as a “large amount” for normal weather conditions. The April-May and October transition months are not considered “normal” due to the larger than normal probability of significant load forecast error.

Extreme weather days are defined as days in which the forecast peak temperature for ERCOT is projected to be higher than 95 degrees, or the forecast high temperature is lower than 30 degrees, or days in which ERCOT has issued a Security Notice. On extreme weather days, ERCOT will purchase an amount of NSRS equal to the largest unit online for on-peak hours, and may purchase amounts of NSRS much greater than this amount in extreme circumstances.

ERCOT will use the following in determining the amount of NSRS needed:

1.	Review the weather forecast for the next day and see if it differs significantly from the current day.

2.	If the next day forecast is “similar” to the current day forecast, and the current day forecast high temperature is <95 degrees in Dallas/Ft. Worth or Houston, and the current day low temperature is greater than 30 degrees, and the current day generation plan shows >4600 MW of spinning reserve (including RRS) online all day long, and the current month is not April, May, or October, THEN no NSRS is considered to be required all day for the next day.

3.	Else: Purchase NSRS using the following:

	If the current month is April, May or October, then purchase NSRS in amounts equal to the largest unit online for the hours projected within 85% of peak hour.

	If today’s and tomorrow’s ERCOT high temperature is projected above 95 degrees in Dallas/Ft. Worth or Houston, then purchase NSRS in amounts equal to the largest unit online for the hours projected warmer than 95 degrees.

	If tomorrow’s low temperature forecast is projected below 30 degrees in Dallas/Ft. Worth or Houston, then purchase NSRS in amounts equal to the largest unit online for the projected morning load pickup hours and hours projected within 85% of peak hour.

	Purchase amounts of NSRS equal to the largest unit online for hours in which the Day Ahead operator estimates spinning reserves online will drop lower than 4600 MW.

### Replacement Reserve Requirements

Replacement Reserve Service (RPRS) is procured by ERCOT if resources are needed to provide additional Zonal or Local Balancing Energy Service.  The RPRS analysis performs look-ahead analysis of the physical system for each of the hourly time intervals in either the Day Ahead or Adjustment Period Time frame. Based on the study, RPRS procurements are made if the submitted resource plans indicate capacity inadequacy or potential zonal congestion requiring additional resources or local congestion requiring specific resources. The procured capacity from these resources must be bid into the Balancing Energy Service market, which clears during the Operating Period.

The purpose of RPRS is to insure the availability of capacity from resources such that the energy from those resources would be available to solve the following system security violations:

- Local congestion

- ERCOT system capacity insufficiency

- Zonal Congestion

Also, the procurement mechanism for resolving local congestion needs to be separate from the mechanism for resolving capacity insufficiency/ zonal congestion. The procurement for resolving local congestion is based on a minimal cost approach that uses generic costs for resources and the procurement for capacity insufficiency and zonal congestion is based on a minimal cost approach that uses resource bids or generic costs from the participants.  Hence, the objective of the proposed RPRS market clearing is to minimize the total bid-based cost of the RPRS bids for the whole duration of the Replacement market (i.e. the whole day for Day Ahead Market and the specified time duration for the Adjustment Period) subject to the unit specific temporal constraints and ERCOT transmission security constraints not being violated.

Figure - Flow diagram for the RPRS market clearing engine

### Balancing Energy Requirement

Balancing Energy is incremental or decremental energy dispatched by ERCOT for eachby 15-minute Settlement Interval to meet the difference between generation scheduled by the market and ERCOT System load.  Local Balancing Energy Service is also used to resolve local transmission congestion. Balancing Energy is deployed by ERCOT with the goals that (1) Regulation Service in either direction not be depleted during the interval, (2) Regulation Service up and down energy is deployed in each Settlement Interval such that the net energy in regulation is minimized, and (3) to provide for frequency control when frequency is high, especially during minimum load intervals. The latter will be included in the determination of BES Down Bid Percentage Requirements. ERCOT will estimate Balancing Energy needs based on the actual Load, the difference in forecasted Loads and bilateral schedules, deployed Regulation Service, and forecasted Congestion.

The following three-step approach is used to determine amount and location of BES needed in each Settlement Interval.

Step 1 is to determine balancing energy service needs to resolve generation-load balance and Zonal Congestion.Balancing Energy Service is procured with Local Congestion ignored, i.e., only recognizing Zonal Congestion.

The output of the application will be zonal MCPE, shadow prices of Zonal Congestion and

Portfolio Incremental/Decremental balancing service MW needed by QSE and CM zone.  An estimate will be made of Resource-specific MW outputs (this is intermediate solution and does not indicate resource-specific dispatch instructions).

Step 2 is to determine balancing energy service needs to resolve Local Congestion as well as generation-load balance and Zonal Congestion.

- The transmission security analysis is performed using the Resource Plan for both the starting with the dispatch and  each units minimum/maximum capabilities MW solutions from Step 1  for checking operational security.

- If no operational constraint violation is detected, the solution from Step 1 is the final solution to the balancing energy service market.

- When any Local Congestion is violated, the solution proceeds as follows:

3.1) The resource-specific incremental premium is taken as the prices for resource-specific incremental bids.

3.2) The resource-specific decremental premium is taken as the prices for resource-specific decremental bids.

3.3) The portfolio balancing service MW solutions by QSE and CM zone obtained in Step 1 are kept  the same at the portfolio level.

3.4) The amount and location of balancing energy service is recalculated with the sum of the incremental and decremental bids cleared due to relieve Local Congestion across all zones.  All constraints, including Zonal Congestion and OC, are observed. The objective of Step 1 solution is to minimize the cost of Local Congestion. The output of the application will be as follows:

	Portfolio Incremental/Decremental balancing service MW solutions by QSE and CM zone

	Resource-specific MW outputs (resources that are identified to receive premiums will be sent resource-specific dispatch instructions.)

	Shadow prices of Local Congestion

Step 2 is to determine balancing energy service needs to resolve generation-load balance and Zonal Congestion.Balancing Energy Service is procured while maintaining Local Congestion constraints

- The output of Step 2 will be zonal MCPE, shadow prices of Zonal Congestion and Portfolio Incremental/Decremental balancing service MW needed by QSE and CM zone.  An estimate will be made of Resource-specific MW outputs (this is intermediate solution and does not indicate resource-specific dispatch instructions).

- A complete list of all RPRS unit commitment with the ability for the Operator to de-select any individual unit/hour.

### Step 3 is to determine balancing energy service needs to resolve generation-load balance and Zonal Congestion subject to the local constraint deployments made in step 2.

### The market clearing prices from Step 3 will represent the marginal cost for the solution of each constraint and will be produced as an output of the mathematical optimization application. The output of the application will be as follows:

	zonal MCPE

	shadow prices of Zonal Congestion

	Portfolio Incremental/Decremental balancing service MW needed by QSE and CM zone

	Resource-specific MW outputs (this is intermediate solution and does not indicate resource-specific dispatch instructions).

	A final RPRS unit commitment for all study hours

### Minimum Balancing Energy Service (BES) Down Bid Percentage Requirement

For Frequency Control (to correct high frequency)

Minimum Balancing Energy Service (BES) Down Bid Percentage Requirement will be set for all intervals of each day. A down bid percentage requirement will be determined to allow for correcting for high frequency. This is a potential need for all intervals, but is especially needed during minimum load periods.

ERCOT will normally calculate the minimum down balancing requirement for QSE’s as follows.

ERCOT will collect the amount of BES (up and down) deployed and the sum of schedules for each operating period for the two time frames described below:

- The monthly data one year previous to the month to be posted.

- The month to date data on the current month (month previous to the month being analyzed). This interval will generally end on the 19th of the month previous to the month to be posted as the requirements will be posted on the 20th of the preceding month.

From this data ERCOT will calculate the mean balancing energy deployedand a standard deviation An amount of down balancing service expected to be sufficient to avoid exhausting the down balancing stack 99.9% of intervals will then be calculated. This amount of down balancing service, expressed as a percentage, will normally be posted as the down balancing percentage requirement. (Note – single outlying historic deployments may be selected in place of this statistical analysis if review indicates such a requirement is justified.)

ERCOT may post this value to be the continuous requirement, or may further analyze the needs to provide a varying requirement by:

- Zone

- On Peak and Off Peak hours

ERCOT may change this requirement during the month if experience shows that the initially proposed requirement is insufficient.

##### For Congestion Management

If a need for additional down balancing is required in a single zone, or zones for congestion management, it is expected by ERCOT that zonal assessment of the data discussed above will allow detection and posting of the need in advance. If this expectation is not correct, ERCOT may adjust the zonal down balancing requirement to address specific congestion events observed.

### Responsive Reserve (RRS) Requirement

The ERCOT Operating Guides set the RRS requirement at 2300 MW for all hours under normal conditions. The Operating Guides allow ERCOT to increase that requirement under extreme conditions. The 2300 MW requirement was derived based on studies done in the past to determine the amount of Responsive Reserve that might be required to prevent the shedding of firm load upon the simultaneous loss of the two largest generation units in ERCOT.

One type of Responsive Reserve is Interruptible Responsive Reserve. Interruptible Responsive Reserve is Load Acting as a Resource (LAAR) that is automatically interrupted when system frequency decreases to 59.7 Hz. The ERCOT Protocols state, “The amount of Resources on high-set under-frequency relays providing RRS will be limited to 50% of the total ERCOT RRS requirement. ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation to be deployed as prescribed in section 6.4.1, Standards for Determining Ancillary Services Quantities.”

Self arranged Responsive Reserve used to fulfill a QSE’s Responsive Reserve requirement must be at least (100% – minimum LAAR %) % from generation resources. ERCOT procured Responsive Reserve to provide the difference between the 2300 MW system requirement and the amount of Responsive Reserve self arranged by all QSEs must also be at least (100% – minimum LAAR %) % from generation resources.

If the minimum LAAR % level specified in the Protocols is changed, that change will be reflected in these requirements.

### Responsive Reserve % LAAR

Protocols allow ERCOT to set the percentage of Responsive Reserve that may be served by LAARs. ERCOT calculates the maximum secure RRS that can be provided by LAARS by performing stability analysis of several power flow cases modeling the ERCOT transmission/generation system at different states. ERCOT will examine these models response to generator trip events and the response of LAARS/Generation to recover frequency using different generation/LAAR amounts. Unless indicated otherwise by these studies or adverse operating experience, LAARs will be allowed to provide up to 50% of the ERCOT Responsive Requirement of 2300 MW.

ERCOT has the option to use only the current years data if its analysis indicates a significant change in market behavior since the previous year.

ERCOTs maximum deployment of RRS is defined as the amount procured, divided by 10 multiplied by 1.25.  This restrictions is specified in  protocol section 6.10.5.3 which states “ERCOT shall limit the deployment of RGS Services to QSEs for each control cycle equal to one hundred twenty five percent (125%) of the total amount of RGS Service in ERCOT divided by the number of control cycles in ten (10) minutes. “