## Updated Event Code Matrix
Meter vs. MV90 Event codes | [5 empty] | KEEP or DELETE? | WHY?
*** UPDATED Listing 09-30-05 ***
EVENT | ERCOT Definition | METER
|  | ION | Mark V | Q1000 | JEMSTAR
Hardware Errors | Various hardware malfunctions (i.e. Modem card/chip, measurement chip, CPU, etc..) Fatal or not. | Various | Various | Various | Various | KEEP | There are various hardware errors that are contained in this category. However, the complete lists of what these types of errors may include are still in development between the meter manufacturers and ITRON's TIM development group. Once TIM development is complete for MV90xi, this category can be reviewed for relevancy and broken into more defined errors, if needed.
Firmware Errors | Firmware has a checksum error, watchdog time out error, or other problem with the firmware. Fatal or not. | Various | Various | Various | Various | KEEP | There are various firmware errors that are contained in this category. However, the complete lists of what these types of errors may include are still in development by some meter manufacturers. Once the lists are completed for all meter manufacturers, this category can be reviewed for relevancy and broken into more defined errors, if needed.
RAM and ROM Errors | Bad spots in memory identified via checksum or other means. | 3 | 6 | OA | NA | KEEP | Memory errors indicate a serious issue that may, or may not, corrupt the data storage area of the meter. These errors aid in the verification of the interval data.
Pulse Overflow Errors | The maximum size value for the number of pulses per interval in Load Profile has been exceeded. Does not apply to meters that store/report data in Engineering Units. | DC | 2C | NA | NA | KEEP | Energy that exeeds the meters recording and storage thresholds is generally lost and not accounted for. A Pulse Overflow error can also identify if a metering circuit is been improperly sized, or the energy requirements of the circuit require adjustments to the metering equipment, such as CT's and PT's/VT's.
Low Battery Condition | Low battery has been sensed during initial power up, daily self checks, after power outages, or any other means to check for a low battery condition. | CA | 1 | NA | NA | KEEP | A low battery typically does not have any effect on the meter's data recording and storage abilities, as long as power is not lost to the meter. If a battery is low, and power is lost, then all data stored in the meter is also lost. Identifying this type of error allows batteries to be scheduled for replacement prior to a power loss that may result in data loss.
AC Power Up | When the Meter Electronics are power up either via Aux Pwr or connected to System Power | OE | NA | NA | OE | KEEP | The time of the power being restored to the meter allows for exact identification of the length of the power outage. Ths ensures accurate editing of meter data and outage tracking/reporting to occur. This error works in tandem with the AC Power Down error.
AC Power Down | When the Meter Electronics loses power either by Aux Pwr or connected to System Power | OD | OD | OD | OD | KEEP | The time of a power loss is critical in the validation of a meter point's energy flow, and system operation. This error works in tandem with the AC Power Up error.
Configuration Changed | Meter has been reprogrammed, or any meter programming where a settlement metering parameter is changed. | 12 | 12 | 12 | NA | KEEP | This could indicate that a meter is malfunctioning, and possibly resetting itself, if this error occurs during periods where no party is accessing the meter. It could also indicate unauthorized access to a meter.
Clock Set/Change | The Meter real time clock has been set/changed by external sources | 15, 16 | 6B | 6B or 85 | 15, 16 | KEEP | This event should only be logged during times that authorized parties are accessing the meter. It is also critical to the validation of the data by ensuring that energy is recorded in the interval that the energy actually flows.
Test Mode Activation | Meter going into and out of Test Mode | 51,52 | 51, 52 | 51, 52 | 51, 52 | KEEP | Indicates when a party has placed the meter in "test mode", thereby affecting the values stored in the interval. A meter is Test Mode may not be recording and storing the energy within the interval. This typically occurs during periods of physical access when a Technician is performing work for the metering curcuit. Logging this event facilitates correct meter editing to ensure that correct energy values are used for settlements
Inactive Potential | System Phase Voltage has been lost on any phase. | A0, A1, A2 | A0, A1, A2 | DB | NA | KEEP | Critical error that may identify a serious metering circuit error, such as a loss of a PT/VT.
|  | NA | = No Event Information Retrieved by MV90's TIM
Note on D4: ERCOT: Firmware Ver 4.0 or later
Note on E8: 062404: Marks interval load profile status of "V", but not logged in event log.
Note on E9: 062404: In meter diagnostics, but not logged in event log
Note on E15: PRS 062404: "DB" code for any phase
Note on F4: pvinton: As of 10-29-04, there is one (1) JEMSTAR Meter in service.

## ION
Conversion of IONTM events to MV-90 events
EFFECT VALUE | EFFECT HANDLE | MV-90-EVENT | MV-90 EVENT CODE
Power down |  | Power outage, short int | 0D
Power up |  | Power outage, short int | 0E
Time about to be changed |  | Time reset occurred | 15
Time changed |  | Time reset occurred | 16
9011 |  | Watchdog timeout | 0C
Battery low |  | Battery fail | CA
Master reset complete |  | Reset occurred | D4
54608 |  | Program malfunction detected | 3
700 |  | Modem failure | 98
Meter password change |  | Password changed | 13
Pulsed |  | Billing reset | 45
On | 61DDh | Meter over Kw demand | 2C
On | 61E1h | Meter over voltage unbalance | D5
On | 61DEh | Meter over threshold phase a | DC
On | 61DFh | Meter over threshold phase b | DC
On | 61E0h | Meter over threshold phase c | DC
On | 6063 | Potential voltage loss on (phase not listed) | EB
On | 6064 | Potential voltage loss on (phase not listed) | A0
On | 6065 | Potential voltage loss on (phase not listed) | A1
On | 6066 | Potential voltage loss on (phase not listed) | A2
On | 6063 | Voltage sag | E6
On |  | Voltage imbalance | D5
Disturbance |  | Power quality event start | E2
Normal |  | Power quality event end | E3
Partial factory init |  | Configuration changed | 12
Hardware security |  | Password changed | 13
Hardware security enabled |  | Password changed | 13
Changed setup |  | Configuration changed | 12
DST started |  | Fall daylight savings time change | 18
DST on |  | Fall daylight savings time change | 18
Time sync |  | Recorder clock set new time | 16
Time change |  | Recorder clock set new time | 16
|  | Output control relay toggle | 44
Password security en |  | Changed password
Telnet locked out |  | Attempted access with invalid password
Value changed |  | Operating parameter changed
Unknown - text event
Test Mode Activated |  | Test Mode Activated | Added to TIM by ITRON/Power Measurement

## Mark V
MARK V EVENT CODE MAP
Transdata EMS 50/ MARK V Firmware Version 4.0 or later only
TRANSDATA MARK V EVENT | MV90 EVENT | MV90 Event Code
Voltage Sag- Phase A | Voltage Sag | E6
Voltage Sag- Phase B | Voltage Sag | E6
Voltage Sag- Phase C | Voltage Sag | E6
Voltage Swell - Phase A | Voltage Swell | E7
Voltage Swell - Phase B | Voltage Swell | E7
Voltage Swell - phase C | Voltage Swell | E7
Voltage Outage - Phase A | Potential A Inactive | A0
Voltage Outage - Phase B | Potential C Inactive | A2
Voltage Outage - Phase C | Potential B Inactive | A1
Breaker Operation - Phase A | Breaker Operation | E8
Breaker Operation - Phase B | Breaker Operation | E8
Breaker Operation - Phase C | Breaker Operation | E8
Volt. Under Limit - Phase A | Low Voltage Limit | E9
Volt. Under Limit - Phase B | Low Voltage Limit | E9
Volt. Under Limit - Phase C | Low Voltage Limit | E9
Angle Outside Limit - Ph A | Phase Angle Limit | EA
Angle Outside Limit - Ph B | Phase Angle Limit | EA
Angle Outside Limit - Ph C | Phase Angle Limit | EA
Cur Below Limit - Phase A | Low Current Limit | EB
Cur Below Limit - Phase B | Low Current Limit | EB
Cur Below Limit - Phase C | Low Current Limit | EB
PF Outside Limit - Phase A | Power Factor Limit | EC
PF Outside Limit - Phase B | Power Factor Limit | EC
PF Outside Limit - Phase C | Power Factor Limit | EC
Ex input 1 Open (hi) | Status Input Opening - # | 32
Ex Input 1 Closed (lo) | Status Input Closure - # | 31
EX input 2 Open(hi) | Status Input Opening - # | 32
Ex input 2 Closed (lo) | Status Input Closure - # | 31
Control Output 1 Open | Relay Opened - Relay # | 36
Control Output 1 Closed | Relay Closed - Relay # | 84
Control Output 2 Open | Relay Opened - Relay # | 36
Control Output 2 Closed | Relay Closed - Relay # | 84
Control Output 3 Open | Relay Opened - Relay # | 36
Control Output 3 Closed | Relay Closed - Relay # | 84
Control Output 4 Open | Relay Opened - Relay # | 36
Control Output 4 Closed | Relay Closed - Relay # | 84
Control Output 5 Open | Relay Opened - Relay # | 36
Control Output 5 Closed | Relay Closed - Relay # | 84
Battery Time Over Limit | Battery Failure | 1
EPROM Diagnostic Error | EPROM Failure | 9D
RAM Diagnostic Error | RAM Error Detected | 6
Register Watchdog Tripped | Watchdog Timer Error | 0C
A/D Watchdog Activated | Watchdog Timer Error | 0C
Communications Error | Communications Session Interrupted | 43
Dial Out Unsuccessful | Call-in Failure | 20
Meter Power Turned off | AC Power Down | 0D
Maximum Demand Reset | Billing Reset | 45
Recorder Data Retrieved | Data Log Uploaded | 8C
Register programmed | Configuration Changed | 12
Time Changed | Time or Date Changed | 6B
Register reading changed | Pre-Set Register Values | 5C
A/D Programmed /recalibrated | Calibration Change | ED
Test Mode Initiated | Start of Test Mode | 51
Test Mode Exited | End of Test Mode | 52
Daylight Savings Time | Unrecognized recorder Event Code/ Spring Daylight Savings Time changed/ Fall daylight Savings Time Changed | 74/19/18
Recorder Time Sync | Recorder time Sync. | EE
TOU Season Change | Season Change | EF
Register Rollover | RAM Buffer Overflow/Initialization | 0A
Demand register overflow | RAM Buffer Overflow/Initialization | 0A
Recorder Overflow | RAM Buffer Overflow/Initialization | 0A
Demand over limit - start | Meter Over Threshold – Channel # | 2C
Demand Over Limit End | Meter Return Within Limits – Channel # | B9
Harmonic Alarm - start | Customer Alarm 1 | 75
Harmonic Alarm - END | Customer Alarm 1 | 75
Event Log Data Retrieved | Event Log Uploaded | 8D
All Meter Data Reset | Metering Equipment Reset | D4
Any Other Event | Unrecognized Recorder Event Code | 74

## Q1000
Q1000 Event Code Map
Manufacturers Description | MV90 Message | MV90 Event Code
MASS_MEM1_EOI | RAM Buffer Overflow/Initialization | ‘0A’
MASS_MEM2_EOI | RAM Buffer Overflow/Initialization | ‘0A’
DEMAND_RESET | Operating Parameter changed | ‘11’
LOSS_OF_PHASE | Phase Failure | ‘D6’
LOSS_OF_PHASEA | Phase Drop-out(Phase, short/Long) | ‘DB’
LOSS_OF_PHASEB | Phase Drop-out(Phase, short/Long) | ‘DB’
LOSS_OF_PHASEC | Phase Drop-out(Phase, short/Long) | ‘DB’
REGISTER_FREEZE | Freeze Meter Readings | ‘47’
CLCOK_ERROR | Recorder Clock Malfunction Detected | ‘17’
ENTER_TEST_MODE | Start of Test Mode | ‘51’
LEAVE_TEST_MODE | End of Test Mode | ‘52’
POWER_OUTAGE | AC Power Down | ‘0D’
CALL_ON_SCHEDULE | Scheduled Call-in | ‘95’
METER_REPROGRAM | Configuration Changed | ‘12’
CLOCK_ADJUSTMENT | Time or Date Changed | ‘6B’
ALARM1_ON | Customer 1 Alarm | ‘75’
ALARM2_ON | Customer 2 Alarm | ‘76’
ALARM3_ON | Alarm Activated | ‘89’
ALARM4_ON | Alarm Activated | ‘89’
ALARM5_ON | Alarm Activated | ‘89’
ALARM6_ON | Alarm Activated | ‘89’
ALARM7_ON | Alarm Activated | ‘89’
ALARM8_ON | Alarm Activated | ‘89’
ALARM9_ON | Alarm Activated | ‘89’
ALARM10_ON | Alarm Activated | ‘89’
ALARM11_ON | Alarm Activated | ‘89’
ALARM12_ON | Alarm Activated | ‘89’
ALARM13_ON | Alarm Activated | ‘89’
ALARM14_ON | Alarm Activated | ‘89’
ALARM15_ON | Alarm Activated | ‘89’
ALARM16_ON | Alarm Activated | ‘89’
ALARM17_ON | Alarm Activated | ‘89’
ALARM18_ON | Alarm Activated | ‘89’
ALARM19_ON | Alarm Activated | ‘89’
ALARM20_ON | Alarm Activated | ‘89’
ALARM21_ON | Alarm Activated | ‘89’
ALARM22_ON | Alarm Activated | ‘89’
ALARM23_ON | Alarm Activated | ‘89’
ALARM24_ON | Alarm Activated | ‘89’
EXTERNAL_INP0_ON | Status Input Opening | ‘6E’
EXTERNAL_INP1_ON | Status Input Opening | ‘6E’
EXTERNAL_INP2_ON | Status Input Opening | ‘6E’
EXTERNAL_INP3_ON | Status Input Opening | ‘6E’
EXTERNAL_EOI | Status Input Opening | ‘6E’
BEFORE_DST_ENTRY | Spring DST Change | ‘19’
AFTER_DST_ENTRY | Spring DST Change | ‘19’
BEFORE_DST_EXIT | Fall DST Change | ‘18’
AFTER_DST_EXIT | Fall DST Change | ‘18’
INVALID_PASSWORD | Attempted Access With Invalid Password | ‘1E’
AUTO_TIME_ADJUST | Auto Timeset Performed | ‘85’
| Unrecognized Recorder Event Code | ‘74’

## JEMSTAR
JEMSTAR Event Code Map
Note/Manufacturer’s Description | MV90 Event Message | MV90 EventCode
Power outage | AC Power Down | 0D
Power outage | AC Power Up | 0E
Time set | Recorder Clock Set – previous time | 15
Time set | Recorder Clock Set – new time | 16
Test mode | Start of Test Mode | 51
Test mode | End of Test Mode | 52
Daylight Saving Time Change | DST Change – Previous Time | 4A
Daylight Saving Time Change | DST Change – New Time | 4B
Billing Period Reset | Billing Reset | 45
Register Freeze | Freeze Meter Readings | 47
Register Preset | Pre-Set Register Values | 5C

## Meter Populations 09-30-05
TYPE | 2005-04-12 | 2005-09-30
ION 8300/8400 | 822 | 795
MARK V | 326 | 334
Q1000 | 77 | 75
JEMSTAR | 1 | 1
TOTAL | 1226 | 1205