| OGRR Number | 154 | OGRR Title | Generator Protection Requirements |  |
| --- | --- | --- | --- | --- |
| Timeline | Normal | Recommended Action |  | Approve |
| Operating Guide Section(s) Requiring Revision |  | 3.1.4.6, Protective Relaying Requirement |  |  |
| Proposed Effective Date |  | November 1, 2005 |  |  |
| Priority & Rank Assigned |  | TBD |  |  |
| Revision Description |  | Describes the operating conditions under which generators should stay connected |  |  |
| Procedural History |  | - On 8/27/04, OGRR154 was posted. - On 9/15/04, Centerpoint posted comments. - On 10/4/04, AEP posted comments. - On 10/18/04, CPS posted comments. - On 10/19/04 and 10/20/04, FPLE posted comments. - On 11/08/04, AEP posted comments. - On 6/21/05, OGRTF posted comments. - On 7/22/05, OWG considered this OGRR. - On 8/11/05, ROS considered this OGRR. |  |  |
| OWG Recommendation |  | OWG recommends approval of OGRR154 as revised by OGRTF comments. |  |  |
| Summary of OWG discussion |  | The OGRTF chair explained that the OGRTF comments of 6/21/05 are a result of the consensus reached at a special OGRTF meeting for OGRR154. No further comments have been received since posting of those comments. |  |  |
| ROS Recommendation |  | On 8/11/05, ROS voted unanimously to recommend approval of OGRR154 as recommended by OWG. |  |  |
| Summary of ROS discussion |  | No discussion. |  |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT |  |  |  |
| MARKET SEGMENT |  |  |  |
| Consumer |  |  |  |
| LSE: General, Including NOIE |  |  |  |
| LSE: CR & REP |  |  |  |
| QSE |  |  |  |
| Resource |  |  |  |
| TDSP |  |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | David A. Darnell |
| Company | OGRTF |
| Segment | N/A |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| Centerpoint 091504 | Revised language to ensure generator terminal voltage trip points are consistent with setpoints. |
| AEP 100404 | Revised language adding to Centerpoint's volgate/time curve |
| CPS 101804 | Expresses concern over setpoint values. |
| FPLE 101904 | Requests exception for induction generators. |
| FPLE 102004 | Agrees with original OGRR language. |
| AEP 110804 | Recommends referral to technical committee. |
| OGRTF 062105 | Revised language consensus from special OGRTF meeting |

Proposed Operating Guide Language Revision

#### 3.1.4.6	Protective Relaying Requirement

The Facility’s generation machine characteristics and plant design shall incorporate the under-frequency firm Load shedding philosophy and criteria defined in Operating Guide 2.9. Requirements for Under-Frequency Relaying.  Inherent in this philosophy is the idea that all generators remain on line until all three steps of firm Load shedding have been executed.  In addition, Generation Resources must remain connected to the transmission system during the following operating conditions:

  - Generator terminal voltages are within five percent (5%) of the rated design voltage and volts per hertz are less than one hundred five percent (105%) of generator rated design voltage and frequency;

  - Generator terminal voltage deviations exceed five percent (5%) but are within ten percent (10%) of the rated design voltage and persist for less than 10.0 seconds;

  - Generator volts per hertz conditions are less than one hundred sixteen percent (116%) of generator rated design voltage and frequency and last for less than 1.5 seconds;

  - A transmission system fault (three-phase, single-phase or phase-to-phase) is cleared by the protection scheme coordinated between the Generation Entity and the TDSP on any line connected to the generator’s transmission interconnect bus, provided such lines are not connected to induction generators described in Protocol Section 6.5.7.1, Generation Resources Required to Provide Voltage Support Service Installed Reactive Capability, item (7).

The generation Facility shall have protective relaying necessary to protect its equipment from abnormal conditions as well as to be consistent with protective relaying criteria as described in Operating Guide Section 5: Planning.

Within thirty (30) days of ERCOT’s request, Generation Resources shall provide ERCOT with the operating characteristics of any generating unit’s equipment protective relay system or controls that may respond to temporary excursions in voltage with actions that could lead to tripping of the generating unit.

Generating Resources required to provide VSS shall have and maintain the following capability:

(1)	Over-excitation limiters shall be provided and coordinated with the thermal capability of the generator field winding and protective relays in order to permit short-term reactive capability that allows at least eighty percent (80%) of the unit design standard (ANSI C50.13-1989), as follows:

Time (seconds)		10	30	60	120

Field Voltage %		208	146	125	112

After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.

(2)	Under-excitation limiters shall be provided and coordinated with loss-of-field protection to eliminate unnecessary generating unit disconnection as a result of operator error or equipment misoperation.