## Slide 1: ERCOT Operational Audit 2005
August 1 - August 19, 2005

## Slide 2: Overview
There were a total of 251 items assessed
  241 compliant
  10 non-compliant
Compliant Score of 96%
Solutions to the 10 non-compliant items are provided in the following slides.

## Slide 3
Conclusions
The 10 non-compliant findings in the audit have been addressed and solutions are provided. The beneficial aspects of an Operational Audit are demonstrated by the improvements observed in this year’s performance. Actions taken as a result of previous audits contributed to this year’s success.

## Slide 4: Issue 1: Steps performed out of sequence on Day Ahead Replacement
Day Ahead Desk Section 2.12: Initiate ERCOT Day Ahead Replacement Capacity Market. Steps not performed in sequence
Solution:
  It was determined that performing these steps out of order did not have an adverse impact on the desired result. The procedure was changed to remove the sequential requirement. Expected Completion Date: Completed

## Slide 5: Issue 2: Time delay before executing Hour Ahead Study not observed
Operating Period Desk Section 2.1.1: Execute Hour Ahead Study
Solution:
  The note is being changed to instruct the system operator to verify the real-time balancing market has cleared by utilizing a message screen in the MOI. This will be covered in Continuous Training Cycle 2. Expected Completion Date: October 13, 2005

## Slide 6
Issue 3: Omitted step recalling NSRS without recognized exception
Operating Period Desk Appendix 3.4: How to deploy NSRS
Solution:
  The two steps that were omitted were not needed to recall NSRS. The recall is only needed for one market participant who believes they have corrected the issue. The appendix will be changed to include one procedure for deploying NSRS and one for recalling NSRS. Expected Completion Date: October 13, 2005

## Slide 7
Issue 4: Steps performed out of sequence when issuing an Alert
Transmission and Security Desk Section 2.5.3: Issue an Alert
Solution:
  It was determined that performing these steps out of order did not have an adverse impact on the desired result of the procedure. A note has been added to inform the operator the sequence is only a recommendation. Expected Completion Date: Completed

## Slide 8
Issue 5: Did not print Hot Line call log
Transmission and Security Desk Section 2.5.3: Issue an Alert
Solution:
  It is an Operating Guide requirement (Section 2.3.2) to record or file all written or electronic dispatch instructions and acknowledgements as soon as practicable after the issuance of the dispatch instruction. The importance of the hot line call log will be covered in Continuous Training Cycle 2. Expected Completion Date: October 13, 2005

## Slide 9
Issue 6: Did not ensure MP or RAP available
Transmission and Security Desk Section 2.1.2: RTCA Congestion Management and 2.2.6: Mitigation Plans
Solution:
  There is a RAP-C Enhancement Project which is due in production in mid-November. When this tool is delivered, all RAPs, MPs, PCAPs, and RAPCs that are posted will be modeled; eliminating this issue. Expected Completion Date: November 15, 2005

## Slide 10
Issue 7: Steps performed out of sequence when issuing an Alert
Frequency Control Desk Section 2.6.3: Issue an Alert
Solution:
  It was determined that performing these steps out of order did not have an adverse impact on the desired result of the procedure. A note has been added to inform the operator the sequence is only a recommendation. Expected Completion Date: Completed

## Slide 11
Issue 8: Did not check ENS or MIS notifications
Frequency Control Desk Section 2.6.3: Issue an Alert
Solution:
  It is imperative that the system operators have checks and balances during real time operations. When a situation arises that requires the posting of a message, system operators should verify the posting occurred by either viewing the message system or by consulting with other system operators. The importance of this verification will be covered in Continuous Training Cycle 2. Expected Completion Date: October 13, 2005

## Slide 12
Issue 9: Logging error
Frequency Control Desk Section 2.4.1: Monitor SCE for each QSE
Solution:
  It is required that system operators log any pertinent information regarding an event in the electronic logs. The importance of the logging requirement will be covered in Continuous Training Cycle 2. Expected Completion Date: October 13, 2005

## Slide 13
Issue 10: Unscheduled Generator Testing
Frequency Control Desk Section 2.3.1: Unscheduled Generator Testing
Solution:
  This procedure was removed from the Frequency Desk and the Shift Supervisor’s procedure was enhanced to govern the process in the future. Expected Completion Date: Completed

## Slide 14: Conclusion
The Operations Department showed improvement from the last Operational Audit.
In the last three years we have improved on the Compliance Operational Audit
We understand the benefit of the audit and welcome the input to better our operational readiness

## Slide 15
Questions