## Slide 1
Hurricane Rita

## Slide 2: ERCOT Preparation
ERCOT started alerts to QSEs and TOs on 9/21
Did a site failover of EMMS system Austin Taylor
Procured satellite voice communications between ERCOT and TOs in impact area
Cancelled planned transmission outages as of Friday, 9/23
Delayed scheduled implementation of Release 4 on 9/28
Requested QSEs to:
  Staff all plants unless safety dictated otherwise
  Notify ERCOT of all evacuated plants
  Keep Resource Plans, Schedules, Bids up to date
  Bid in all available capacity into BES market, particularly DBES
  Be prepared to take plants off line quickly if requested by ERCOT

## Slide 3: ERCOT Preparation (cont.)
Distributed frequency control guidelines to all QSEs and Generators in case of loss of communication ERCOT QSE Generator
Created link for hurricane updates on ercot.com
Scheduled MP conference calls for September 23, 24, 25
Set up separate 24-hour phone hot lines for media and market participants for issues not concerning real time operations beginning 9/23
Arranged for extra ERCOT System Operators and Supervisors to come in if needed
Stated intent to keep market operating as long as possible

## Slide 4: Rita Track
120 MPH
50 MPH

## Slide 5: ERCOT Customer Outages
Customer outages started 17:00 on 9/23 in Galveston/Houston (CenterPoint)– hit a peak of 715,000 at 07:00 9/24
Customer outages started 06:00 on 9/24 in Lufkin/Nacogdoches/Tyler (TXUED) – up to 70,000 customers ultimately affected
Vast majority of customer outages due to distribution system damage
Service to almost all customers in ERCOT restored by 9/30

## Slide 6: ERCOT Transmission and Generation Outages
Transmission
  16 - 138KV lines
  1 – 138/69KV autotransformer
  9 – 69 KV lines
  1 – 69 KV substation
  All back in service by 06:00 9/28
  No 345 KV outages
Generation
  One plant (76 MW) forced out by storm
  Twelve of 30 plants in Houston area were shut down before the storm

## Slide 7: ERCOT Summary
The ERCOT system remained stable throughout the storm
No significant communications problems with Market Participants
ERCOT market systems functioned normally
Experienced record September peak temperatures and demands in the four days following the storm without operational problems
However …………

## Slide 8: Entergy Hit Very Hard
Transmission Outages – 82% of system
  4 – 500 KV lines
  28 – 230 KV lines
  87 – 138 KV lines
  161 – 69 KV lines
  293 substations
Affected 300,000 Entergy Texas customers
East Texas was isolated from rest of Entergy system
Generation deficient in East Texas

## Slide 9: Block Load Transfers (BLTs)
On 9/25 discussions started about possibility of BLTs from Entergy to ERCOT
Decision to close normally open Crosby-Dayton 138 KV tie between CenterPoint and Entergy
  Critical Houston water supply pumps on Trinity river
  Line energized the evening of 9/26
  Entergy started putting load on line on 9/27
  Limit ~ 175 MW
138 KV tie between TXUED and Deep East Texas Electric Coop at Huntington
  Energized on 10/1
  Limit ~ 70 MW

## Slide 10: State and Federal Action
On 9/26 the State Emergency Operations Center created a Tiger Team created to determine how service can be restored in Entergy area ASAP
Actions:
  Governor issued order suspending eminent domain requirements for temporary facilities
  On 9/27 PUCT issued order suspending CCN requirements and allowing ERCOT TDSPs to extend service in Entergy area
  DOE agreed to issue order maintaining ERCOT’s FERC exemption for these emergency connections to Entergy