## ERCOT Operations Report

## ROS & OWG

## September 2005

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 9/4/2005 13:37 | 59.890 | 46091 | 115 | -1241 | 100 MW resource lost. |
| 9/9/2005 1:07 | 60.123 | 31353 | -297 | 248 | -1140 (-170) |
| 9/9/2005 2:19 | 60.106 | 29667 | -248 | -177 | Excessive BES deployed. |
| 9/12/2005 6:34 | 60.108 | 34550 | -100 | -62 | Excessive BES deployed. |
| 9/20/2005 19:50 | 59.899 | 51956 | 740 | 210 | 1 interval late compensating for lighting load. |
| 9/21/2005 3:23 | 60.112 | 30237 | -520 | 381 | QSE A did not receive deployments. QSE B SCE due to NDC testing. QSE C OOMed down but could not follow due to LSL. |
| 9/22/2005 9:37 | 60.112 | 36148 | -18 | 745 | Multiple QSE did not receive deployments for this interval. Site fail over performed at ERCOT at 09:15. |
| 9/22/2005 20:28 | 60.112 | 46193 | -1038 | 87 | Storms causing erratic load pattern. |
| 9/23/2005 2:15 | 60.105 | 29255 | -520 | 235 | High ERCOT SCE 02:00 - 02:15. |

| Disturbance Data |  |  |
| --- | --- | --- |
| 9/1/05 11:38 | 59.896 | 310 MW |
| 9/12/05 1:38 | 59.823 | 540 MW |
| 9/14/05 4:57 | 59.882 | 480 MW |
| 9/27/05 0:30 | 59.850 | 475 MW |
| 9/29/05 1:15 | 59.770 | 770 MW |

| Deployed Responsive (21) (Reported Above) 9/1/05 11:38:28 | 9/12/05 5:53:24 | 9/22/05 6:09:22 |
| --- | --- | --- |
| 9/3/05 22:05:18 | 9/12/05 19:47:12 | 9/22/05 10:16:48 |
| 9/4/05 13:36:58 | 9/14/05 4:57:28 | 9/22/05 19:33:52 |
| 9/5/05 19:16:16 | 9/18/05 22:03:20 | 9/25/05 10:36:44 |
| 9/7/05 1:15:42 | 9/20/05 5:25:14 | 9/27/05 0:30:10 |
| 9/8/05 1:20:02 | 9/20/05 19:45:30 | 9/27/05 19:07:20 |
| 9/12/05 1:38:40 | 9/21/05 19:36:12 | 9/29/05 1:15:20 |

# Locations and Relative Activity of Congestion Management

| Historical OOMC/RMR | Sept 04 | August 05 | Sept 05 |
| --- | --- | --- | --- |
| DFW | 88 | 75 | 69 |
| E RIO | 74 | 101 | 96 |
| W RIO | 56 | 28 | 39 |
| Laredo | 81 | 93 | 90 |
| Bryan Area | 23 | 93 | 91 |
| Corpus | 30 | 33 | 33 |
| Northeast | 0 | 18 | 2 |
| North | 0 | 8 | 4 |
| Western | 0 | 21 | 4 |
| Houston | 0 | 9 | 2 |
| San Antonio | 2 | 0 | 5 |
| Austin | 0 | 0 | 1 |
|  | 418 | 479 | 436 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overloaded Element | # Days |
| --- | --- | --- |
| Gibbons Creek - Bryan East - Greens Prairie | Texas A&M - Dansby 138kv | 30 |
| Marion - Hill Country - Skyline 345kv | Schertz -Parkway 138kv | 22 |
| Marion - Zorn - Clear Spring 345kv | Zorn - Seguin 138kv | 15 |
| North Denton 138/69kv auto | North Sanger - Spring 138kV | 9 |
| Lytton Springs - Zorn & Austrop 345kv | San Marcos - Canyon LCRA 138kv | 7 |
| Austrop 345/138kv Auto | Austrop 345/138kv Auto | 6 |
| La Palma - Rio Hondo 345kv | Rio Hondo La Palma 138kv | 5 |
| Menard 138/69 auto | Ballinger - Paint Rock 69kv | 5 |
| Greenville Steam T1 69kv | Greenville Steam T2 69kv Auto | 3 |
| Marion 345/138kV Auto | Sequin - Zorn 138kv | 3 |
| North Denton 138/69kv T1 auto | Denton Steam - 138/69kv AT1 | 3 |
| North McAllen - North Edinburg 138kv | North Edinburg - MVEC NW Edinburg 138kv | 3 |
| Coleto Creek - Kenedy 138kv | Elmendorf - Eagle Creek 138kV | 2 |
| Fisher Rd-Oklaunion-Bowman 345kV | Lake Pauline 138/69 Auto | 2 |
| Leon Creek - Pleasanton 138kv | Eagle Creek - Elmendorf 138kv | 2 |
| Midland East - Odessa EHV 345kv | Odessa Sw. - Moss Sw 138kv | 2 |
| North McAllen - North Edinburg 138kv | North Edinburg - Magic Valley 138kv | 2 |
| Abilene Mulberry Creek - Oklaunion 345kv | Vernon - Grayback 69kv | 1 |
| Austrop - Sandow 345kv | Gideon to Butler 138kv | 1 |
| Austrop-Lost Pines 345 | Fayett-Salem 345kV | 1 |
| Bates 138/69kv auto | Bates - Palmhurst 69kv | 1 |
| Braunig - Elmendorf 138kv | Leon Creek - Elmendorf 138kv | 1 |
| Burnet - Wirtz 138kv | Buchanan - Burnet 69kv | 1 |
| Comanche Peak Units 1 & 2 | Asherton - West Conoco 138kv | 1 |
| Fisher Road Switch - Bowman Switch 345kv | Vernon - Grayback 69kv | 1 |
| La Palma - Loma Alta 138kv | La Palma - Cavasos 69kv | 1 |
| LaPalma 345/138kv Auto | Rio Hondo - LaPalma 138kv | 1 |
| Lon Hill - North Edinburg 345kv | Lon Hill - Stratton 138kv | 1 |
| McNeil - Round Rock 138kv | McNeil - Howard Lane 138kV | 1 |
| North Denton 138/69kv Auto | Spencer - Denton Steam 69kv | 1 |
| Oklaunion - Fisher Road - Bowman 345kv | Grayback - Vernon 69kv | 1 |
| Rio Hondo - LaPalma 345kv | Rio Hondo - LaPalma 138kv | 1 |
| Sandow - Temple Sw 345kv | Sandow Auto 1 | 1 |
| Sandow Unit 4 | Sandow 345/138kv auto | 1 |
| Skyline - Nacogdoches | Randolph Field - Weiderstein138kv | 1 |
| STP-Skyline-Hill Country 345kv | Blessing - Lolita 138kv | 1 |
| Tradinghouse - Venus 345kv | Tradinghouse - Lake Creek | 1 |
| Tri-Corner - Trindad 345kv | Forest Grove - Mabank Tradinghouse - Venus | 1 |

New RAP

- None

| South to Houston | 19 |
| --- | --- |
| South to North | 14 |
| North to Houston | 5 |
| North to West | 2 |
| West to North | 1 |

- New Procedures/ Forms/Operations Bulletins

| 09/30/2005 | POB 217 | T&S Desk TC - Block Load Transfer. |
| --- | --- | --- |
| 09/29/2005 | POB 216 | T&S Desk TC - Procedure to Cancel OOMEs |
| 09/29/2005 | POB 215 | T&S Desk TC - Level 2 & 3 Outages |
| 09/29/2005 | POB 214 | T&S Desk TC - West Area Action Plan |
| 09/29/2005 | POB 213 | FCD - V2R32 |
| 09/27/2005 | POB 212 | FC Desk Temporary Change - DC Ties. |
| 09/29/2005 | POB 211 | Transmission & Security Desk - V3R59 |
| 09/20/2005 | POB 210 | FC Desk - Emergency Site Failover. |
| 09/20/2005 | POB 209 | OP Desk - V2R13 |
| 09/20/2005 | POB 208 | Shift Supervisor - Root Cause Analysis |
| 09/12/2005 | MOB 27 | Automation of PRR 420 |

Blackout/Load Shed incidences and major system voltage problems

9/26	20 MVA of load was lost at 13:05 in Galveston County. A 138kV line from PH Robinson – Loma Alta – Hitchcock – West Galveston – Moody Reit failed due to damage from Hurricane Rita. A conductor came apart and was on the ground between West Galveston and Hitchcock. PH Robinson – Loma Alta - Hitchcock was restored at 14:28. Hitchcock – West Galveston – Moody Reit was restored at 21:58.

9/27	20 MW of load was lost at 02:16 in Travis County. A fire on a138/12 kV transformer caused the 138kV bus to clear opening 138kV lines Howard Lane to Jollyville, McNeil, and Techridge. Low voltage was experienced on the distribution system causing the loss of up to 200 MW of load. All load was restored by 04:55. the bus and 138kV lines were restored at 08:05.

Voltage Instructions

9/1	13:55	2 kV raise instruction given in Northeast Zone.

9/22	07:41	voltage instructions in South Zone (high voltage on 138 kV system).

9/24	07:35	2 kV lower instruction given in Coast Zone.

9/28	22:55	3 kV raise instruction given in the North Central Zone.

Major Computer Problems, Enhancements & Fixes

None

Communication

9/20 	Held IE 16:00 and IE 17:00.  Significant scheduling error detected

9/23 – 9/25	lost ICCP communication with a TDSP when they transferred to their back up facility.

ERCOT peak (Unofficial)

9/28	17:00  59,345

| Transmission Alerts |  |  |  |
| --- | --- | --- | --- |
| 9/1 | 16:00 - 21:45 | Flatonia 138/69 | Yoakum 138/69 |
| 9/1 | 16:00 - 21:45 | North Denton 138/69 | North Sanger - Spring |
| 9/1 | 11:45 - 21:45 | San Miguel 138/69 | Derby - Pearsall 69 |
| 9/1 | 11:45 - 21:45 | San Miguel Switchyard - Sigmor | Kenedy Switch - Kenedy Sub |
| 9/2 | 15:55 - 19:00 | Lewisville 345/138 | Carrollton NW - Lakepointe |
| 9/2 | 16:10 - 19:00 | North Denton 138/69 | North Sanger - Spring |
| 9/2 | 16:15 - 19:00 | Walnut Springs 138/69 | Olsen - Sycamore |
| 9/4 | 14:35 - 19:30 | San Miguel 138/69 | Derby - Pearsall |
| 9/12 | 16:30 -20:30 | San Miguel 138/69 | Derby - Pearsall |
| 9/13 | 13:00 | South to North | CSC |
| 9/13 | 15:00 - 20:00 | San Miguel 138/69 | Derby - Pearsall |
| 9/14 | 13:00 - 20:00 | San Miguel 138/69 | Derby - Pearsall |
| 9/14 | 14:58 - 20:00 | Whitney to Stephenville | Olsen - Sycamore |
| 9/15 | 14:45 - 24:00 | Fisher Road to Oklaunion | Lake Pauline 138/69 |
| 9/15 | 6:23 - 11:30 | Oklaunion - Mulberry Creek | voltage violations |
| 9/15 | 13:02 - 22:00 | San Miguel 138/69 | Derby - Pearsall |
| 9/16 | 00:00 - 01:00 | Fisher Road to Oklaunion | Lake Pauline 138/69 |
| 9/16 | 14:50-19:30 | Garza-Bates | voltage violations |
| 9/16 | 14:30-19:30 | Marion-Zorn/Clear Spring-Marion | Zorn-Seguin |
| 9/16 | 06:30-19:30 | San Miguel 138/69 | Derby - Pearsall |
| 9/17 | 06:50 - 15:30 | Menard 138/69 | Ballinger - Paint Rock |
| 9/17 | 15:30 - 20:00 | San Miguel 138/69 | Derby - Pearsall |
| 9/18 | 6:20 - 7:20 | Menard 138/69 | Ballinger - Paint Rock |
| 9/18 | 14:30 - 20:00 | San Miguel 138/69 | Derby - Pearsall |
| 9/19 | 15:58 - 24:00 | Loop 337 - GPI Switch | Seguin - Seguin West |
| 9/19 | 13:06 - 18:40 | Asherton 138/69 | Uvalde 138/69 |
| 9/19 | 13:04 - 17:15 | East 138/69 | Atkins - Briarcrest |
| 9/19 | 15:59 - 24:00 | Loop 337 - Comal | Seguin - Seguin West |
| 9/19 | 16:01 - 24:00 | Marion - Skyline & Hill Country | Marion 345/138 |
| 9/19 | 16:00 - 24:00 | Marion - Zorn & Clearsprings | Kendal - Comfort |
| 9/19 | 16:03 - 24:00 | Marion 345/138 | Schertz - Parkway |
| 9/20 | 00:00 - 02:10 | Loop 337 - GPI Switch | Seguin - Seguin West |
| 9/20 | 16:31-19:15 | Pawnee to Calaveras | Elmendorf - Eagle Pass. |
| 9/20 | 16:29-20:50 | San Miguel 138/69 | Derby - Pearsall |
| 9/20 | 13:02-19:15 | Tri-Corner - Trindad | Forest Grove to Mabank |
| 9/20 | 00:00 - 02:10 | Loop 337 - Comal | Seguin - Seguin West |
| 9/20 | 00:00 - 02:10 | Marion - Skyline & Hill Country. | Marion 345/138 |
| 9/20 | 00:00 - 02:10 | Marion - Zorn & Clearsprings | Kendal - Comfort |
| 9/20 | 00:00 - 02:10 | Marion 345/138 | Schertz - Parkway |
| 9/20 | 12:50-19:15 | Marion 345/138 | Zorn to Seguin |
| 9/21 | 12:28-13:49 | Greenville Steam 138/69 | Greenville Steam 138/69 |
| 9/21 | 13:49-20:45 | San Miguel 138/69 | Derby - Pearsall |
| 9/21 | 13:50-15:45 | Skyline to Nacogdoches | Randolph Field -Weiderstein |
| 9/21 | 12:20-20:45 | Marion 345/138 | Zorn to Seguin |
| 9/22 | 15:08-23:45 | Gibbons Crk T1 and T3 | Gibbons Creek T2 345/138 |
| 9/22 | 15:11-21:30 | Asherton Auto | Uvalde 138/69 |
| 9/22 | 15:11-21:30 | Eagle Pass-Hamilton | Uvalde - La Pryor |
| 9/22 | 15:10-23:45 | Marion 345/138 | Zorn to Seguin |
| 9/22 | 15:39-21:30 | San Miguel 138/69 | Derby - Pearsall |
| 9/22 | 15:17-21:30 | Whitney-Stephenville | Olsen - Sycamore |
| 9/23 | 15:30 - 22:00 | Gibbons Creek T1 & T3 345/138 | Gibbons Creek T2 345/138 |
| 9/23 | 12:45 - 22:00 | Asherton 138/69 | Uvalde - La Pryor |
| 9/23 | 15:30 - 22:00 | Batesville - Pearsall | Moore - Downie |
| 9/23 | 15:30 - 22:00 | Downie - Moore | Batesville - West Batesville |
| 9/23 | 15:00 - 22:00 | La Palma 345/138 | Rio Hondo - LaPalma |
| 9/23 | 7:00 - 13:20 | Marion 345/138 | Zorn - Seguin |
| 9/23 | 10:15 - 11:20 | North Denton 138/69 | Locust - Hickory |
| 9/23 | 12:00 - 22:00 | San Miguel 138/69 | Derby Sub - Dilley Sub |
| 9/24 | 14:00 - 20:00 | Asherton 138/69 | Uvalde - La Pryor |
| 9/24 | 14:00 - 20:00 | Batesville - Pearsall | Moore - Downie |
| 9/24 | 14:00 - 20:00 | Downie - Moore | Batesville - West Batesville |
| 9/24 | 14:00 - 20:00 | La Palma 345/138 | Rio Hondo - LaPalma |
| 9/24 | 14:00 - 20:30 | Marion 345/138 | Zorn to Seguin |
| 9/24 | 14:00 - 20:00 | San Miguel 138/69 | Derby - Pearsall |
| 9/25 | 14:00 -23:00 | Asherton 138/69 | Uvalde - La Pryor |
| 9/25 | 14:00 -23:00 | Marion - Zorn & Clearsprings | Zorn to Seguin |
| 9/25 | 14:00 - 23:00 | Marion 345/138 | Zorn to Seguin |
| 9/25 | 14:00 -23:00 | San Miguel 138/69 | Derby - Pearsall |
| 9/26 | 15:00 - 18:45 | Galveston 26th St - Tiki Island | voltage violations |
| 9/26 | 15:00 - 16:10 | Temple - Bell County | Seaton 138/69 Auto |
| 9/27 | 17:30 - 22:30 | Gibbons Crk T1 and T3 | Gibbons Creek T2 345/138 |
| 9/27 | 17:30 - 22:30 | Asherton 138/69 | Uvalde - La Pryor |
| 9/27 | 20:30 - 23:30 | McNeil LCRA - Round Rock | Round Rock NE - Hutto |
| 9/27 | 17:30 - 20:30 | PH Robinson - South Shore | Freeway Park - Dickinson |
| 9/27 | 14:00 - 22:30 | San Miguel 138/69 | Derby - Pearsall |
| 9/28 | 16:00 - 22:30 | Gibbons Creek T1 & T3 345/138 | Gibbons Creek T2 345/138 |
| 9/28 | 15:15 - 22:30 | San Miguel 138/69 | Derby - Pearsall |

| Other Alerts, OCN, & Emergency Notifications |  |  |  |
| --- | --- | --- | --- |
| 9/1 | 1:45 - 10:20 | Alert | Capacity Shortage indicated in resource plans for hours 15 to 18 |
| 9/1 | 00:45 - 1:45 | OCN | Capacity Shortage indicated in resource plans for hour 17 |
| 9/5 | 16:00 - 19:00 | Transmission Emergency | Asherton - W. Conoco |
| 9/8 | 09:40 -18:35 | Alert | Capacity Shortage indicated in resource plans for hours 17 to 18 |
| 9/8 | 08:40 - 9:40 | OCN | Capacity Shortage indicated in resource plans for hours 16 to 18 |
| 9/9 | 04:35 - 15:00 | Alert | Capacity Shortage indicated in resource plans for hours 16 to 18 |
| 9/9 | 03:00 - 04:35 | OCN | Capacity Shortage indicated in resource plans for hours 16 to 18 |
| 9/13 | 0:30 - 2:30 | OCN | Capacity Shortage indicated in resource plans for hours 15 to 17 |
| 9/14 | 03:45 - 10:30 | Alert | Capacity Shortage indicated in resource plans for hours 16 to 18 |
| 9/14 | 02:00 - 03:45 | OCN | Capacity Shortage indicated in resource plans for hours 16 to 18 |
| 9/19 | 07:05 - 17:15 | Alert | Capacity Shortage indicated in resource plans for hour 17 |
| 9/19 | 05:46 - 07:05 | OCN | Capacity Shortage indicated in resource plans for hour 17 |
| 9/21 | 13:35 | Alert | Hurricane Rita. |
| 9/21 | 14:33 | OCN | Release #4 delayed |
| 9/21 | 00:20-13:37 | OCN | Hurricane in Gulf of Mexico with >20% chance making land fall in Texas. |
| 9/22 | 0:15 | Alert | Hurricane Rita. |
| 9/22 | 0:15 | OCN | Release #4 delayed |
| 9/23 | 0:15 - 12:00 | OCN | Release #4 delayed |
| 9/23 | 0:15 - 24:00 | Alert | Severe weather alert for imminent hurricane strike on Texas Gulf Coast. |
| 9/24 | 02:00 - 24:00 | OCN | Extreme Wet Weather for East Texas. |
| 9/24 | 00:15 - 24:00 | Alert | Severe weather alert for imminent hurricane strike on Texas Gulf Coast. |
| 9/26 | 02:45 - 18:00 | Alert | Capacity Shortage indicated in resource plans for hours 15 to 18 |
| 9/26 | 01:00 - 0245 | OCN | Capacity Shortage indicated in resource plans for hours 15 to 18 |

Other

9/15	00:00	Oklaunion – Fisher Road – Bowman 345 kV circuit and Fisher Road 345/138 kV transformer tripped.

9/18	08:16	Cleared 345 kV bus at Graham, tripping 4 345 kV lines and a 345/138 kV transformer.   All elements returned to service by 10:16.

9/19	15:00	Cleared both 138 kV busses at Zorn station.  6 138 kV lines and two 345/138 kV transformers.  All elements returned to service 9/20 at 05:30.