ERCOT Operations Report

ROS & OWG

July 2003

Frequency control issues (High or Low Frequency) 59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 7/1/03 0:07 | 59.897 | 35069 | -354 | -913 | -1966 (-1096) |
| 7/2/03 6:04 | 60.138 | 31148 | -281 | 819 | 955 (-903) |
| 7/9/03 1:05 | 60.164 | 30967 | -509 | 343 | -1311 (-472) |
| 7/11/03 5:59 | 60.122 | 31336 | -991 | 685 | 219 ( - 392) |
| 7/19/03 6:10 | 59.892 | 30297 | -378 | -193 | -1319 (1087) |
| 7/19/03 8:22 | 59.898 | 33072 | 925 | -204 | 425 (230) |
| 7/22/03 6:50 | 60.105 | 33829 | -817 | 1210 | 40 (-16) |
| 7/25/03 6:07 | 59.897 | 31797 | -210 | 59 | 1878 (1150) |
| 7/25/03 6:49 | 60.102 | 32591 | 106 | 554 | > .1 Hz for 4 sec |
| 7/28/03 9:33 | 60.103 | 39686 | -104 | 439 | > .1 Hz for 2 sec |
| 7/28/03 14:53 | 59.898 | 52491 | 768 | -435 | > .1 Hz for 20 sec |
| 7/29/03 22:02 | 59.896 | 46033 | -470 | -739 | -2105 (885) |

Lost Resources / Communicating Deployments

| 7/3/03 6:00 | 60.122 | MOI Problems |
| --- | --- | --- |
| 7/5/03 11:03 | 60.12 | MOI Problems |
| 7/7/03 9:30 | 59.877 | 550 MW Unit Trip |
| 7/9/03 1:08 | 59.806 | 1150 MW Unit Trip |
| 7/15/03 12:09 | 59.803 | 2 Units Tripped, 1250 MW Total |
| 7/16/03 6:13 | 59.888 | 650 MW Unit Runback and Trip |
| 7/17/03 17:12 | 59.899 | 440 MW Trip |
| 7/19/03 13:57 | 59.887 | 410 MW Unit Trip |
| 7/19/03 14:50 | 59.886 | 4 Units tripped, 460 MW total |
| 7/19/03 15:05 | 60.102 | Overshoot from Trip |
| 7/21/03 15:09 | 59.888 | 450 MW Unit Trip |
| 7/31/03 13:54 | 59.81 | 800 MW Unit Trip |

Locations and Relative Activity of Congestion Management

*Days of units purchased for some time in the area described.  Data taken from daily reports and is approximate.  For global overview purposes only.

New Procedures/ Forms/ Operations Bulletins

| 07/25/2003 | ERCOT Power Operations Bulletin 31 | Procedure for Control of transmission system loading within N-1 Thermal Contingency Criteria using Real Time Contingency Analysis |
| --- | --- | --- |
| 07/24/2003 | ERCOT Power Operations Bulletin 30 | Procedure for Control of transmission system loading within N-1 Thermal Contingency Criteria using Real Time Contingency Analysis |
| 07/16/2003 | ERCOT Power Operations Bulletin 29 | Revision of Operating Procedures Development and Maintenance |
| 07/14/2003 | ERCOT Power Operations Bulletin 28 | Revision of Cancelled Outages |
| 07/14/2003 | ERCOT Power Operations Bulletin 27 | Revision of timeline for BES |
| 07/08/2003 | ERCOT Power Operations Bulletin 26 | Revision of Operating Procedures |
| 7/03/2003 | ERCOT Market Operations Bulletin 11 | PRR 369/398 Local Balancing Energy and OOME payment for ERCOT approved aggregated units |

# Security Alert Stage/ Threatcon/ Related issues

Security Threat Alert Yellow (Elevated) maintained through July.

Describe each EECP Occurrence

None.

OCN, Advisory, Alert, Energy Notice and Major Disturbances

7/6	13:45 – 23:30	Transmission Alert issued for the North to Houston interface.

7/7	05:45-17:00	OCN issued for North To Houston.

7/11	05:31-07:25	Communications Alert.  Deployments not being issued by ERCOT.

14-16th 13:25-01:00	Weather Advisory posted due to hurricane conditions.

7/17	08:45-19:00	OCN issued for North To Houston.

Major Weather Related Power System Problems

None

Significant Communication Problems

7/4	19:30-22:27	Replacement Study delayed.  Earlier studies failed due to a

resource with bad data submitted.

7/11	05:31-07:25	Communications Alert.  Deployments not being issued by ERCOT.

ERCOT Digital Certificate expired.

7/19-20  23:20-04:49	2 QSE’s lost OPX Phones.

Major Computer Systems Problems/ Fixes

None

Major system Voltage problems

None

Blackout/Load Shed incidents

None

ERCOT peak for last month (Unofficial)

56239	on 7/22  at 17:00

Update on New Generation

None

Max Temperature

108 F 		 North Central

# New SPS & RAP’s

7/21	Implemented RAP for Double circuit outage of  Allen Switch – Renner 345 +

Allen Switch – Plano Tennison 345 to mitigate the post contingent flow on Allen

Switch Auto Transformer #1.

## Other

RTCA implemented in July.