| PRR Number | 363PRR | PRR Title | IDR Data Start-Stop Times |
| --- | --- | --- | --- |
| ###### Recommended Action |  | Approve |  |
| Proposed Effective Date |  | December 1, 2002 |  |
| Priority & Rank Assigned |  | N/A |  |
| Summary of Impact Analysis |  | None. |  |
| Benefit |  | Assures that TDSPs can match 814_20 maintenance transactions to usage records. |  |
| PRR Background |  | ## Adds language to require TDSPs (and future Meter Reading Entities) to send only whole days of data for all IDR ESI IDs. Establishes a Protocol mandate for providing IDR data in a manner that supports allowing ERCOT to remove the gap validation from the IDR data loading process. The result will be more IDR data loaded and available for settlement. This requirement also facilitates any “backdating” associated to IDR ESI IDs. |  |
| Protocol Revision Subcommittee Recommendation |  | PRS recommends approval as revised. |  |

Recommended Language

### 10.9.2 TDSP Metered Entities

TDSPs will be required to ensure that the meters for which they are responsible comply with the standards for metering Facilities of the relevant Governmental Authority.  In addition, IDRs used for settlement shall conform to the following:

- IDRs must be able to capture energy consumption in increments consistent with, or in fractions of, ERCOT defined settlement time interval (currently fifteen (15) minutes);

- Regardless of data retrieval method, interval data shall be provided on a schedule that supports the requirements of final settlement;

- IDRs must have battery or other energy-storage back-up to maintain time during power outages;

- IDRs must have time synchronization capability;

- Meter clocks used within ERCOT shall be maintained on a time reference that enables the TDSP to submit data on the Central Prevailing Time.  The meter clock shall be synchronized to within at least +/- 5% of the settlement interval when compared to the National Institute of Standards and Technology (NIST) Atomic Clock;

- IDRs may record at increments less than ERCOT defined settlement and be aggregated to the appropriate settlement interval time block by the TDSP prior to the data being sent to ERCOT;

- New and replacement IDRs used for settlement must be able to capture energy in increments of five (5) minutes (excluding memory allocation).  At market open they will be programmed to read at 15-minute intervals; and

- Settlement intervals will divide each hour in the following standard:

XX:00:01 through XX:15:00

XX:15:01 through XX:30:00

XX:30:01 through XX:45:00

XX:45:01 through XX:00:00

- IDR data submitted to ERCOT for Operating Days December 01, 2002 or later will contain only whole days with start times beginning at 00:00:00 and stop times ending at 23:59:59.

| PRR Evaluation |  |
| --- | --- |
| Non-ERCOT Market Comparison | No Comparison conducted. |
| Comments Author | Comments Summary |
|  | None submitted. |