## ERCOT Operations Report

## ROS & OWG

## October 2005

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 10/2/2005 6:02 | 60.114 | 28513 | -888 | 874 | 1400 (540) |
| 10/6/2005 0:12 | 60.118 | 33599 | -103 | 379 | -4820 (-1200) |
| 10/9/2005 1:08 | 60.126 | 22782 | -550 | 199 | 11 minutes above 60.1. At 01:00 procured Down Regulation drops from 1260 to 550. Up balancing across this ramp period is normally countered by Down Regulation, which was not available. |
| 10/17/2005 8:01 | 60.107 | 29444 | -1141 | 538 | Operating period did not account for 08:00 load dip. |
| 10/18/2005 1:05 | 60.101002 | 27083 | -39 | 380 | Balancing up across 01:00 to counter low frequency, Up Regulation, and negative SCE 00:30 - 01:00 |
| 10/20/2005 6:09 | 59.891998 | 29809 | 784 | -855 | 3650 (670) |
| 10/21/2005 1:17 | 60.105 | 26420 | -408 | 182 | -825 (-150). 300 MW VDI issued to reduce generation. |
| 10/24/2005 6:09 | 59.896999 | 27903 | 1192 | -757 | 3740 (1040) |
| 10/28/2005 7:35 | 60.112 | 30088 | -341 | -350 | Operating period did not account for 08:00 load dip. |

| Disturbance Data |  |  |
| --- | --- | --- |
| 10/1/05 11:49 | 59.895 | 685 MW, 3 unit train. 1 unit tripped a few minutes prior to the other 2. |
| 10/4/05 12:51 | 59.863 | 560 MW |
| 10/18/05 13:41 | 59.808 | 4 units, 766 MW |
| 10/19/05 13:53 | 59.893 | 385 MW |
| 10/23/05 22:00 | 59.878 | 470 |
| 10/24/05 2:59 | 59.868 | 660 MW ran back/tripped between 02:55 and 03:00 |
| 10/25/05 10:23 | 59.881 | 2 units, 315 MW |
| 10/30/05 16:08 | 59.799 | 515 MW |
| 10/31/05 7:58 | 59.839 | 655 MW |

Deployed Responsive (27) (Reported Above)

| 10/1/05 11:49 | 10/17/05 11:30 | 10/23/05 22:00 |
| --- | --- | --- |
| 10/1/05 22:07 | 10/18/05 13:41 | 10/24/05 2:59 |
| 10/2/05 9:06 | 10/18/05 22:06 | 10/24/05 6:02 |
| 10/2/05 22:59 | 10/19/05 13:53 | 10/24/05 9:56 |
| 10/4/05 0:06 | 10/19/05 22:04 | 10/24/05 13:01 |
| 10/4/05 12:51 | 10/20/05 6:03 | 10/25/05 10:23 |
| 10/5/05 14:50 | 10/20/05 22:29 | 10/29/05 17:40 |
| 10/9/05 22:04 | 10/23/05 0:14 | 10/30/05 16:08 |
| 10/14/05 22:01 | 10/23/05 1:59 | 10/31/05 7:58 |

Day Ahead Capacity Purchases

| Historical OOMC/RMR | Oct 04 | Sept 05 | Oct 05 |
| --- | --- | --- | --- |
| DFW | 68 | 69 | 42 |
| E RIO | 91 | 96 | 115 |
| W RIO | 60 | 39 | 36 |
| Laredo | 86 | 90 | 52 |
| Bryan Area | 55 | 91 | 54 |
| Corpus | 31 | 33 | 31 |
| South | 0 | 0 | 14 |
| North | 0 | 4 | 6 |
| Western | 0 | 4 | 7 |
| Houston | 0 | 2 | 41 |
| San Antonio | 3 | 5 | 8 |
| Austin | 0 | 1 | 0 |
|  | 433 | 436 | 406 |

New RAP

- None

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| North to Houston | 16 |
| --- | --- |
| South to North | 9 |
| North to West | 4 |
| South to Houston | 3 |

| Contingency | Overload | Days |
| --- | --- | --- |
| Gibbons Creek - Bryan East - Greens Prairie | Texas A&M - Dansby | 20 |
| Marion - Hill Country – Skyline | Schertz -Parkway | 20 |
| Marion - Zorn & Clear Spring | Zorn - Seguin | 17 |
| La Palma - Rio Hondo | Rio Hondo - Magic Valley | 7 |
| WHCCS - Rocky Creek/CPSES – DCSES | Concord transformer | 9 |
| Austrop transformer #1 | Austrop transformer #2 | 4 |
| Lytton Springs - Zorn/Austrop – Zorn | San Marcos - Canyon | 4 |
| Lytton Springs - Zorn/Austrop - Zorn | Zorn transformer #1 | 4 |
| Ennis Switch - Desoto Switch | Sterrett - Waxahachie Pump | 3 |
| La Palma - Rio Hondo | South McAllen - Las Milpas | 3 |
| Morgan Creek – Eskota | Eskota transformer | 3 |
| Bowie - Patterson Street | Bowie transformer #1 | 2 |
| Farmersville - Monticello SES | Allen Switch AXFMR 2 | 2 |
| Jacksboro Sw- Willowcreek | Stephenville-Lingleville Tap | 2 |
| Lytton Spring - Zorn/Austrop - Zorn | Canyon-Rohr | 2 |
| Sandow - Temple | Uvalde - Asphalt Mines | 2 |
| Austrop - Sandow | Gideon-Butler | 1 |
| Bates - Garza | Bates-North Edinburg 69 KV | 1 |
| Coleto Creek - Kennedy Switch | Leon Creek - Pleasanton | 1 |
| Dilley Switch - San Miguel | Derby - Pearsall 69kv | 1 |
| Elkton - Tricorner & Martin Lake | Tyler NW transformer | 1 |
| Ferguson - Wirtz | Ferguson - Wirtz | 1 |
| Greenville Steam transformer 1 | Greenville Steam transformer #2 | 1 |
| Hamilton Rd - Sonora | Uvalde - Asphalt | 1 |
| Jack County - Hill Top | Jack County - Balsara | 1 |
| Kendall - Fredericksburg | Comfort - Raymond Barker | 1 |
| McNeil LCRA - Round Rock | McNeil -Howard Tap | 1 |
| Morgan Creek-Odessa Ector | Big Spring Sw.-Big Spring West | 1 |
| Parker Switch - EMSES & Roanoke | Flat Rock - Azle | 1 |
| Pawnee - Lon Hill | Kenedy Switch - Kenedy Sub | 1 |
| Pawnee-Calavares | Leon Creek-Pleasanton | 1 |
| Sandow transformer | Sandow - Elgin Switch | 1 |
| Salem AT3 transformer | Gideon-Austrop 138 | 1 |
| Sargent Rd-Water Mill Sw | Lake Hubbard-Duck Creek Tap | 1 |
| Skyline - Marion & STP | Schertz -Parkway | 1 |
| Ennis Switch - Desoto Switch | Sterrett - Waxahache Pump 1 | 1 |
| Watermill - Tricorner & Trinidad | Kleburg Tap - Seagoville | 1 |
| Zorn - McCarty Lane | Henne - Comal | 1 |

- New Procedures/ Forms/Operations Bulletins

| Date | Power Operations Bulletin | Subject |
| --- | --- | --- |
| 10/27/2005 | Power Ops Bulletin 223 | T&S Desk - Voltage Issues and Contingency Analysis |
| 10/10/2005 | Power Ops Bulletin 222 | T&S Desk - Emergency Site Failover |
| 10/10/2005 | Power Ops Bulletin 221 | SS Manual - Monitor QSEs Which Under Perform in Supplying Ancillary Services |
| 10/10/2005 | Power Ops Bulletin 220 | DA Desk - VDI Instruction |
| 10/10/2005 | Power Ops Bulletin 219 | FC Desk - Emergency Site Failover |
| 10/03/2005 | Power Ops Bulletin 218 | T&S Desk - Voltage Support. |

Blackout/Load Shed incidences and major system voltage problems

Voltage Instructions

10/15	07:57	2 kV lower instruction given in North Zone.

10/16	07:48	2 kV lower instruction given in North Zone.

Major Computer Problems, Enhancements & Fixes

10/05	00:00 Implemented R-4 on the production systems.

Communication

10/5	Held 14:00 interval.  Two NSRS deployments for IE 14:15 caused problems in the MOI.

10/6 	Held 04:00 interval.  MOI would not accept the offset entry.

ERCOT peak (Unofficial)

10/05	17:00 52,200

| Alerts and OCN |  |  |  |
| --- | --- | --- | --- |
| 01-Oct-05 | 23:00 | OCN | Capacity insufficiency for operating day Sunday 10/02/05 hours 16:00 - 18:00 |
| 02-Oct-05 | 01:00 - 17:00 | Alert | Capacity insufficiency for operating day Sunday 10/02/05 hours 15:00 - 18:00 |
| 02-Oct-05 | 13:50 - 15:30 | Transmission Alert | Post Contingency limit on Bates-North Edinburg |
| 02-Oct-05 | 0:15 - 01:00 | OCN | Capacity insufficiency for operating day Sunday 10/02/05 hours 16-18. (Continuation from 10/01/05) |
| 03-Oct-05 | 4:00 - 16:30 | Alert | Capacity insufficiency for operating day Monday 10/03/05 hours 15:00 -18:00 |
| 03-Oct-05 | 2:00 - 04:00 | OCN | Capacity insufficiency for operating day Monday 10/03/05 hours 15:00 -18:00 |
| 03-Oct-05 | 16:05 - 23:15 | Transmission Alert | Howard Lane Tap - McNeill LCRA |
| 05-Oct-05 | 15:30 - 19:00 | OCN | Capacity insufficiency for hour 17:00 |
| 10-Oct-05 | 14:30 -23:45 | Transmission Alert | Dilley Switch - North Laredo loads Asherton - North Laredo |
| 10-Oct-05 | 16:00 -cont. | Transmission Alert | Ingleside Cogen loads Dupont Switch Ingleside - Air Liquide |
| 10-Oct-05 | 14:30 - 16:00 | Transmission Alert | Kingsville - Lon Hill loads Falfurrias transformer |
| 10-Oct-05 | 14:30 -23:45 | Transmission Alert | San Miguel transformer loads Pearsall - Derby Sub |
| 10-Oct-05 | 14:30 -23:45 | Transmission Alert | San Miguel Switchyard - Sigmor loads Kenedy Switch - Kenedy Sub |
| 11-Oct-05 | 00:15 -23:45 | Transmission Alert | Ingleside Cogen loads Dupont Switch Ingleside - Air Liquide |
| 17-Oct-05 | 18:00 - 21:00 | Transmission Alert | Coppell - Lewisville loads Coppell - Roanoke |
| 17-Oct-05 | 10:15 - 24:00 | Transmission Alert | Ingleside Cogen loads Dupont Switch Ingleside - Air Liquide |
| 18-Oct-05 | 01:35 -23:00 | Alert | Capacity insufficiency for hours 16:00 - 18:00. |
| 18-Oct-05 | 00:20 - 01:35 | OCN | Capacity insufficiency for hours 16:00 -18:00 |
| 19-Oct-05 | 00:13-20:00 | Alert | Capacity insufficiency for hours 17:00 - 21:00. |
| 19-Oct-05 | 13:00 - 19:10 | Transmission Alert | Uvalde -Asphalt 138 kV line loading. |
| 20-Oct-05 | 13:00-18:00 | Transmission Alert | Uvalde -Asphalt 138 kV line loading. |
| 24-Oct-05 | 06:30-10:15 | Alert | Capacity insufficiency for hours 11:00 - 12:00. |
| 24-Oct-05 | 01:30-06:30 | OCN | Capacity insufficiency for hours 11:00 -14:00 |
| 30-Oct-05 | 1:15 - 2:30 | OCN | Capacity insufficiency for hours 20:00 - 21:00. |
| 30-Oct-05 | 2:30 - 20:00 | Alert | Capacity insufficiency for hours 20:00 - 21:00. |

Status of Barney Davis RMR review

ERCOT has reviewed the power factor data from the Corpus Christi area and found lower (worse) load power factors then had been previously assumed.  ERCOT is in the process of reviewing transient stability studies and power flows using these power factors.

ERCOT, with the assistance of AEP, has performed stability and power flow studies for some of the construction periods, and has discovered risks associated with retirement of the Barney Davis generating units.

During some of the required transmission clearances it appears that part of Corpus Christi may be vulnerable to voltage collapse.  ERCOT is reviewing studies of these periods in an attempt to discover a way to mitigate this risk during the outage periods.