SETTLEMENT METERING OPERATING GUIDE

February 5, 2003

[Edited by the MWG 10-21-2005]

[Compare and Merge Documents submitted by:]

[Reliant]

[TNMP]

[ERCOT]

Edited by Market Rules 11/7/05

MWG Review 11/16/2005

In the event of a conflict between this Guide and the ERCOT Protocols, the ERCOT Protocols shall control.

Table of Contents

Section 1:

EPS Metering Facility Requirements

1.1	Purpose and Scope

(1)	The purpose of these guidelines is to outline standards, specifications, procedures and practices for ERCOT Polled Settlement (EPS) Metering Facilities.

(2)	The scope of these guidelines is limited to EPS Metering and to the metering equipment and practices necessary to provide accurate metering of electrical quantities for settlement.

(3)	These guidelines are intended to apply to EPS Metering Facilities. These guidelines are not applicable to measurements intended for local monitoring or for station relaying, control, and operation.  Refer to the appropriate section of the Protocols and Operating Guides for requirements of other metering applications.

1.2	General

(1)	Measurements covered under this guideline include energy quantities used for Settlement Metering as referenced in the Protocols and  this Settlement Metering Operating Guide (SMOG).

(2)	All devices used in EPS Metering shall conform to or exceed standards outlined in the Protocols and this SMOG.

(3)	Test switches shall be installed in the instrument transformer secondaries circuit to provide a means to measure quantities required to certify the facility and allow the application of test quantities to the meter. Test switches should be utilized for all devices in the metering circuit. Test switches shall conform to the latest revision of ANSI C12.9 applicable at time of original installation.

1.3	Current Transformers

1.3.1	Fault Withstand

Current transformers shall be capable of withstanding available fault current levels.

1.3.2	Quantity

(1)	Current transformers shall be installed, one in each phase, for metering of an EPS facility, which is connected to a four-wire wye neutral grounded system or in two phases for metering of an EPS facility, which is connected to a three-wire ungrounded system.

(2)	Current transformers may be installed in two phases for metering of an EPS facility which is connected to a three-wire wye, neutral grounded transmission system if phase-to-ground loads or phase-to-ground sources are not connected between the metering point and the power transformer primary windings. The EPS facility may have power equipment connected that does not provide a path for ground current (e.g. three phase power transformers with delta or ungrounded wye winding connection, phase-to-phase connected single phase power transformers, etc.).

Exclusions are:

(a)	Potential transformers

(b)	Surge protectors

(3)	Transmission and Distribution Service Provider (TDSP) shall verify that all power transformer primary connections behind the metering point are ungrounded delta, ungrounded wye or phase to phase. This verification shall be performed by the TDSP on an annual basis, at each required site certification and any time changes are made to the circuit configuration.

(4)	The EPS Design Proposal one line will need to include designation of all connected power transformers.

- (a)	One line detail must show all tapped power transformers

(b)	When new power transformers are tapped, a new design proposal must be submitted to ERCOT showing the additional tapped power transformer.

5)	A professional engineer registered in the state of Texas shall provide a certification that the three VT - two CT metering is an accurate metering configuration for the specific EPS metering point as specified in this document.  Such certification should be based on the TDSP detailed drawings submitted with the site approval request, with confirmation of site certification by an approved TDSP EPS Meter Inspector.

(6)	TDSP shall be responsible for confirming that the facility meets the requirements outlined above. For metering an EPS facility connected to a three-wire wye neutral grounded transmission system and not meeting these requirements, current transformers shall be installed in each phase.

- 1.3.3	Burden

- (1)	The current transformer burdens shall be kept as small as practical and shall not exceed the burden rating of the current transformer

- (2)

- During annual testing, the total current transformer burden shall be checked by the addition of a known burden to determine that the specified burden capability of the current transformer is not exceeded.  ERCOT may waive the requirement for the burden check, upon receipt of written information from the TDSP that provides the specific reason(s) why this requirement was not met.

- 1.3.4	Secondary Wiring

- (1)

- No splices will be allowed in the current transformer secondary circuit except through the use of terminal block connections.

- (2)	The integrity of the secondary wiring of the current transformers shall be verified at initial certification and at least every three years thereafter.

- (3)	The metering circuit should be limited to highly accurate billing meters and load control transducers.  Relays shall not be connected to the secondary metering circuit.

- 1.3.5	Grounding of Current Transformer Secondary Circuits

- (1)

- A common return conductor shall be utilized for each set of isolated current transformer secondary windings.

- (2)	The common terminals of each set of current transformers shall be grounded at only one point.

- (3)	It is recommended that the ground connection be located at the meter or at the nearest terminal block to the meter.

- (4)	The ground conductor shall be, at a minimum, the same wire size as the smallest polarity conductor in the metering current circuit.

- 1.3.6	Induced Voltage

- (1)	Secondary circuits should be designed and routed so as to avoid the possibility of induced voltages and the effects of high ground fault voltages.

- (2)

- Suitable protection against the effects of fault and switching generated over-voltages should be provided.

- 1.3.7	Paralleling of Current Transformers

Paralleling of current transformers is not recommended.  However, when it is necessary, the following requirements  apply.

- (a)	All transformers must have the same nominal ratio regardless of the ratings of the circuits in which they are connected.

- (b)	All transformers which have their secondaries paralleled must be connected to the same phase of the primary circuits.

- (c)	The secondary circuits shall be connected in a configuration to allow for testing of individual instrument transformers. The secondary circuits shall be paralleled at the meter test switch.

- (d)	There shall be only one ground on the secondary of all paralleled transformers at their common point.  It is recommended that the ground be located at the meter or at the nearest terminal block to the meter.

- (e)	Each current transformer must be capable of supporting n times the connected burden within the accuracy class of the transformers, where n = number of current transformers in parallel.

- (f)	A common voltage must be available for the meter.  This condition is met if the circuits share a common bus that is normally operated with closed bus ties.

- (g)	The meter must have sufficient current capacity to carry the sum of the currents from all the transformers to which it is connected.

- (h)	The secondary leads from all current transformers shall be such that the maximum possible burden placed on any transformer does not exceed its adjusted burden rating, as defined in (e) above.

- 1.3.8	Sizing of Current Transformers

(1)			Current transformers shall be sized for optimum metering accuracy, considering peak, nominal and minimum loads, current transformer rated accuracy, rating factor, and ability to withstand available fault current.

(2)			Optimum metering accuracy may require the use of the following:

- (a)	Rating factor greater than 1.0; and/or

(b)	High accuracy, extended range current transformers.

1.3.9				Exceptions

(1)	Exceptions would include bi-directional EPS metering points in service on October 1, 2000 where under normal conditions (facility is generating electricity), large amounts of power flows into the ERCOT grid; and on occasion, when all generation behind this metering point is off-line, this same metering point will experience small amounts of power flow from the ERCOT grid into the facility. If changes to existing current transformers are required, the metering point shall no longer be classified as “in service on October 1, 2000”.  For these existing installations, the TDSP shall:

- (a)	Ensure good engineering design practices were met for this metering installation

- (b)	Ensure metering equipment meets all applicable ANSI standards

- (c)	Ensure the current transformer is operating within its accuracy range at peak and nominal generation output

(2)	Example of good engineering design practice is when the

current transformers are selected to maintain revenue metering accuracy at expected peak loads and still achieve acceptable accuracy at minimum loads, recognizing that these smaller loads may be outside the demonstrated accuracy range of the current transformer.

(3)	At EPS meter Facilities with an approved Design Proposal, current transformer replacement shall not be required based solely upon advancements in instrument transformer technology.

- 1.4	Voltage Transformers

- 1.4.1	Quantity

- (1)	Voltage transformers for a four-wire wye neutral grounded system (three single-phase units or one three-phase unit) shall be installed, one from each phase conductor to the circuit neutral.

- (2)	Voltage transformers (two single-phase units) for a three-wire ungrounded system shall be installed from phase to common phase.

- (3)	Voltage transformers (three single-phase units or one three-phase unit) for a three-wire wye, neutral grounded transmission system may be installed from phase to ground on the primary and be used for two-stator metering. The TDSP must ensure the following conditions:

- (a)	The EPS Facility does not have equipment that provides a path for ground current (except insulators, surge arresters, voltage transformers) connected to the three-wire wye neutral grounded transmission system.

- (b)	The three metering voltage transformers must be connected to the grounding system of the transmission facility for the voltage reference.

- (c)	The meter potential elements shall be connected from phase to common phase on the secondary of the voltage transformers.

- (d)	The secondary circuit of the metering potentials shall be connected to the grounding system of the transmission facility.

- 1.4.2

- Burden

(1)			The voltage transformer burdens shall be kept as small as practical.

(2)			The total burden/volt-ampere rating of the voltage transformer shall not be exceeded.

- 1.4.3	Protection

Secondary fuses should be of the high-speed, high current interrupting construction with low electrical impedance and the mechanical ruggedness to resist the effects of corrosion and vibration.  The main purpose of fuses shall be for protection of personnel, the transformer, and the secondary wiring against accidental faults or shorts, rather than to protect the voltage components of the measuring devices.  Fuses shall not be placed in the common secondary return or the ground circuit of instrument transformers.

- 1.4.4	Secondary Wiring

- (1)	All secondary wiring shall be designed such that the maximum voltage drop at the metering devices does not exceed 0.3 Volts.  A voltage drop calculation or measurement shall be performed as part of the initial installation.

(2)	The integrity of the secondary wiring of the voltage transformers shall be verified at initial certification and at least every three years thereafter.

- (3)	No splices will be allowed in the voltage transformer secondary circuit except through the use of terminal block connections.

- 1.4.5	Grounding of Voltage Transformer Secondary

- (1)			Each set of voltage transformer secondary windings shall have only one ground.

(2)			It is recommended that the ground connection be located at the meter or at the nearest terminal block to the meter.

- 1.4.6	Induced Voltage

- (1)			Secondary circuits should be designed and routed so as to avoid the possibility of induced voltages and the effects of high ground fault voltages.

(2)			Suitable protection against the effect of fault and switching generated over-voltages should be provided.

- 1.4.7	Loss of Potential

The secondary circuit shall be monitored for loss of potential on each phase.

- 1.5	Metering Facility

- 1.5.1	Specification

- (1)	The environment for the EPS metering equipment shall be designed such as to maintain at all times the operating characteristics as stated by the meter manufacturer.

- (2)	A clear space shall be provided in front of the meter as outlined in the latest revision of IEEE C2, The National Electric Safety Code, Article 125a applicable at time of original installation.

- 1.5.2	Facilities for Testing

Test switches should be located at, or near the metering devices.  Where the test output of the meter is electrical rather than visual, provisions should be made to conveniently measure the test output.

- (a)	The meters and test facilities should be located inside an enclosure or structure that provides adequate protection of the equipment from the environment.

- (b)	Adequate lighting should be provided in the area of meters as required for testing, maintenance and adjustment.

- (c)	Test switches shall be wired to allow individual meters to be removed from service for testing without affecting other meters in the circuit.

- (d)	When an automatic current shorting “relay” test block is used to test meters, meters shall be wired such that the testing of individual meters does not affect other meters in the circuit.

1.6

- Testing and Calibration

- 1.6.1	Test Equipment

Test equipment and test standards used for the testing and/or calibration of instrument transformers and EPS meters shall be certified to values of accuracy and precision which are equal to or better than the accuracy of the equipment under test.

- 1.6.2	Certification of Standards

All field and laboratory test standards shall be certified traceable to the National Institute of Standards and Technology, on the most stringent time schedule required by ANSI or the PUCT Substantive Rules, with a minimum of an annual certification.   The appropriate correction factors shall be utilized to determine percent registration and retained with the standard.

- 1.6.3	Responsibility

Except in those cases where the involved parties agree otherwise, the party installing and controlling the metering installation shall be responsible for any maintenance and calibration.  The meter test personnel shall be qualified to test the metering installation.

- 1.6.4	Notification

- (1)	Notification to ERCOT shall be in accordance with the requirements of  Protocol Section 10, Metering.

- (2)	Parties requesting notification of impending tests shall do so by written request to the TDSP.  The request shall provide contact information of the requestor.

- 1.6.5	Calibration Tolerance

(1)			EPS meters shall meet the percent accuracy tolerances for kWh testing listed in the table below:

#### Series Test Sequence

| % Test Amp | Power Factor | Tolerance % |
| --- | --- | --- |
| 100 | 1.0 | ±0.15% |
| 10 | 1.0 | ±0.15% |
| 100 | 0.5 lagging | ±0.3% |

(2)			The individual elements shall be tested for balance before installation to within ±1.0%.  A final series test sequence shall be performed  after any calibration adjustment.

(3)

kVARh tests shall be performed at 100% and 10% test amps using a phase shift between sixty (60) and ninety (90) degrees from unity power factor.  The percent tolerance for kVARh tests shall be ±0.3%.

- 1.7

- Test Schedules and Records

- 1.7.1	Frequency of Testing

EPS Meters shall be tested in the meter’s test mode on a frequency as defined in the Protocol Section 10, Metering.

- 1.7.2	Test Records

(1)			The TDSP shall keep the meter test records for a period of at least six years after the date of the test.

(2)			Upon written request to the TDSP, the most recent meter test record shall be provided to the designated EPS facility representative or duly appointed agent within 10 business days.

- 1.8	TDSP Responsibility for Documentation Following Facility Testing or Maintenance

The TDSP shall furnish the following EPS Metering Facility information to ERCOT:

- (a)	For routine annual meter tests where no changes to the existing metering facility occur, the TDSP shall forward the EPS Meter Test Reports to ERCOT within 14 Calendar Days of the date of meter test.

- (b)	When changes to the Metering Facility occur that affect settlement data or data retrieval, including calibration errors greater than twice the defined accuracy limit for the Metering Facility, the TDSP shall promptly notify ERCOT and the designated EPS facility representative and make all reasonable efforts to forward site data to ERCOT and the designated EPS facility representative by 10:00 am the Business Day following such changes.

- (c)	Test Forms - EPS Meter test results shall be recorded on approved ERCOT meter test report forms.

- Section 2:

- Failure of ERCOT Communication Facilities

- ERCOT Settlement Communication Link Unavailable for EPS Meters

During a disruption to the ERCOT MDAS Communication Link to EPS Meters, ERCOT shall:

(a)	Make all reasonable efforts to provide general information to TDSPs using voice communications; and

(b)	Inform TDSPs of the methods they shall use to provide meter data to ERCOT during the disruption period.

Section 3:

Documentation for EPS Metering Facilities

3.1	General

The documentation in this section shall be used to meet the requirements outlined in Protocol Section 10, Metering.  ERCOT forms can be found on the ERCOT web site.

3.2	Documentation Requirements

3.2.1	Design Proposal

The design proposal should be provided no less than 45 Calendar Days before the TDSP installation of equipment.

- (a)	Facility Information and Contact Information

- (b)	Metering Facility details

- (c)	One Line drawing of facilities showing metering points

- (d)	Other information as required

3.2.2	Meter Information Package

The Meter Information Package should be provided no less than seven Calendar Days before the TDSP certification of the facility.

- Meter information for the primary and back-up metering installations must include:

- (a)

- MDAS configuration form

- (b)	Other information as required

3.2.3		Site Approval Request Package

The Site Approval Request Package should be provided within 60 Calendar Days after the site has been certified and must include:

- (a)	Site Certification Form.

- (b)	EPS Meter Test Report.

- (c)	Copy of Meter Programming File.

- (d)	TDSP meter multiplier calculation sheet as prescribed in subsection 3.3.

- (e)	TDSP pulse multiplier calculation sheet as prescribed in subsection 3.3.

- (f)	TDSP transformer and line loss compensation calculation sheet as prescribed in subsection 3.3.

- (g)	Certification of instrument transformers.

- Such certification shall include the nameplate information and either a manufacturer’s certificate of test (preferred) or certification by a professional engineer registered in the state of Texas.  Such certification shall include the criteria used to certify that such instrument transformer’s accuracy is in compliance with Protocol Section 10, Metering and this SMOG.

- (h)	Redlined or final as built detailed one line drawing of the complete metering Facility and a three line drawing detailing the metering circuit with TDSP EPS Meter Inspector’s initials.

Note: If a redlined version is supplied, the final as built drawings shall be submitted within 45 Calendar Days of the submittal of the Site Approval Request Package.

(i)	Other information as required.

3.2.4	TDSP Cutover Form

(1)	The TDSP Cutover Form should be submitted 14 Calendar Days before the requested “cutover” date.

(2)	This form shall be submitted by the TDSP to facilitate the transfer of information required to add or remove an EPS meter point in the ERCOT Data Aggregation System.

3.3	Calculation Sheet Requirements

3.3.1		TDSP Meter Multiplier (Internal Registers) Calculation Sheet

This sheet from the TDSP shall convey the process used by the TDSP to calculate the multiplier that shall be applied to the readings retrieved via ERCOT MDAS from EPS Meters to calculate energy.  This sheet shall include the following information:

(a)	The written formula including all information used in the multiplier calculation;

(b)	The multiplier calculation; and

(c)	Rollover calculation for the readings.

3.3.2			TDSP Pulse Multiplier Calculation Sheet

This sheet from the TDSP shall convey the process used by the TDSP to calculate the pulse multiplier that shall be applied to the interval data retrieved via ERCOT MDAS from EPS Meters to calculate energy.  This sheet shall include the following information, as applicable:

(a)	The written formula including all information used in the pulse multiplier calculation;

(b)	The pulse multiplier calculation;

(c)	Rollover calculation for the interval pulse data;

(d)	Pulses per interval at maximum energy output or consumption; and

(e)	Pulses per interval at nominal energy output or consumption.

3.3.3		TDSP Transformer and Line Loss Compensation Calculation Sheet

This sheet from the TDSP shall convey the process used by the TDSP to calculate the transformer and line loss compensation for EPS Meters. This sheet can be accomplished by using the ERCOT posted example of loss calculation shown in Attachment E or a TDSP calculation that meets the same standards.  A TDSP created sheet shall include all information required by Attachment E and the following additional information:

(a)	Formula used to calculate loss compensation;

(b)	Actual values entered into the formula; and

(c)	Logic for calculation of losses if not at full transformer rating.

- EPS Metering Facility Processes and Forms

- ERCOT shall make all reasonable efforts to establish consensus for all revisions to any existing or new procedures or forms in discussions with the MWG prior to implementation.  Such processes and forms shall be located on the ERCOT web site.

Section 4:

EPS Meter Configuration Criteria

  - Standard IDR Channel Assignments

(1)	IDR channel assignment programming for EPS Meters shall conform to the following:

- (a)	Unidirectional meters for Loads:

- (i)	Channel 1 shall record active energy (kWh) flowing out of the ERCOT Transmission System;

- (ii)	Channel 2 shall record reactive energy (kVarh) flowing out of the ERCOT Transmission System (quadrant 1 plus quadrant 2); and

- (iii)	Channel 3 shall record reactive energy (kVarh) flowing into the ERCOT Transmission System (quadrant 3 plus quadrant 4).

- (b)	Bi-directional meters and all generation meters:

- (i)	Channel 1 shall record active energy (kWh) flowing out of the ERCOT Transmission System;

- (ii)	Channel 2 shall record reactive energy (kVarh) flowing out of the ERCOT Transmission System (quadrant 1 plus quadrant 2);

- (iii)	Channel 3 shall record reactive energy (kVarh) flowing into the ERCOT Transmission System (quadrant 3 plus quadrant 4); and

- (iv)	Channel 4 shall record active energy (kWh) flowing into the ERCOT Transmission System.

- (2)	TDSPs may utilize other recording channels, on EPS Meters equipped with more than four channels, for additional data recording provided the utilization of such channels does not interfere with the EPS Meter settlement requirements of the ability of MDAS to retrieve the settlement data.  In addition, the interval length for any optional channels retrieved by MDAS shall be consistent with the settlement data interval.  Use of optional channels other than five through 16 shall require ERCOT approval.

  - Display Modes

- 4.2.1	Normal Display Modes

(1)	ERCOT does not require any display items in the meter’s normal display mode.  The values displayed in the normal display mode will be determined by the TDSP.

(2)	The TDSP shall ensure that EPS meters are programmed in a manner that allows the ERCOT MDAS system to associate internal register readings with the correct recorder interval channel for settlement.

(3)	The meter shall be programmed such that the internal register readings retrieved by ERCOT do not roll over in less than 45 days.

4.2.2	Alternate Display Mode

ERCOT does not require any display items in the meter’s alternate display mode.  The values displayed in the alternate display mode will be determined by the TDSP.

4.2.3	Test Mode Display

ERCOT does not require any display items in the meter’s test mode.  The values displayed in the test mode will be determined by the TDSP.

4.3	Transformer and Line Loss Compensation

Transformer and line loss compensation to EPS Meters shall be performed in accordance with Protocol Section 10, Metering, and the SMOG.

4.4	Flagging of Interval Data for Power Outage

A maximum power outage length of three seconds shall be used for flagging intervals when voltage to the meter’s power supply is lost.

4.5

Programming of Event Log Reporting

Meters shall log and report the events, outlined in Section 6, General Specifications for EPS Meters, when interrogated by the ERCOT MDAS.

4.6

Interval Data Recorder Resolution

4.6.1	Pulse Resolution

The pulse multiplier should be chosen such that, at a minimum, 25% of the maximum allowable pulses per interval are recorded at nominal energy flow, while ensuring that the maximum pulses per interval for the device are not exceeded.  In addition, the capabilities of the ERCOT MDAS system regarding maximum pulses shall not be exceeded.

4.6.2	Engineering Units Resolution

The selected rate of accumulation should be chosen using sound engineering practices to minimize the chances of energy being shifted from one settlement interval to another settlement interval.  In addition, the capabilities of the ERCOT MDAS system regarding engineering units shall not be exceeded.

4.7	Special Applications, Configurations and Unique Situations

(1)	TDSPs are responsible for providing ERCOT with the necessary access to EPS Meters and other information to enable ERCOT to prepare Settlement Quality Meter Data.

(2)	For instance, where there is a generating plant with multiple generators and auxiliary loads, the TDSP must provide appropriate information (i.e. documentation, descriptions, one line diagrams, etc.) to ERCOT to ensure that ERCOT can properly account for the net generator output under all combinations of generation and load (e.g. where only one generator is operating but all auxiliary loads are being supplied).

Section 5:

General Standards for EPS Metering Facilities

5.1	General

The standards for EPS Metering Facilities referred to in this Section provide additional details to the standards referred to in the ERCOT Protocols and apply to EPS Meters used in ERCOT for settlement purposes.

  - General Standards for EPS Metering Facilities

EPS Metering Facilities shall meet the following general standards:

  - Instrument transformers used in Settlement Metering Facilities must meet the requirements in the SMOG.

  - Settlement meters must meet the requirements in the SMOG.

  - Meters must be remotely accessible, 60 Hz, three-phase, programmable and multifunction electronic meters

  - To minimize the loss of energy data during line outage conditions, a highly reliable source of auxiliary power should be utilized.

  - Meters must be capable of being remotely time synchronized by ERCOT (MDAS).

  - Meters must be capable of measuring kWh and kVarh

  - Meters must have battery back-up for maintaining RAM and a real-time clock during outages of up to thirty days

  - The meter must be capable of remote interrogation by the ERCOT MDAS System

  - The meter must be capable of 45 days storage of interval data for each of the required channels

  - Metering equipment connected to the telephone circuit shall be protected with adequate surge protection.

5.3	Detailed Standards for EPS Meters

Section 6, General Specifications for EPS Meters, provides the detailed specifications with which EPS Meters must comply.

5.4	Detailed Standards for Instrument Transformers

Section 7, General Specifications for Instrument Transformers for EPS Metering, provides the detailed specifications with which instrument transformers used with an EPS Meter must comply.

Section 6:

General Specifications for EPS Meters

6.1	Application

This Section applies to all ERCOT Polled Settlement (EPS) Meters.

6.2	Scope

This Section provides the minimum functional and performance requirements for EPS Meters.  Meters used for EPS metering shall comply with all applicable ANSI C12 standards.

6.3	Metering Functions

6.3.1	Measured Quantities

The following energy quantities are required for EPS Meters:

(a)	Kilowatt-hours—flowing out of the ERCOT system;

(b)	Kilovar-hours— flowing out of the ERCOT system (quadrant 1 plus quadrant 2);

(c)	Kilovar-hours— flowing into the ERCOT system (quadrant 3 plus quadrant 4)

(d)	Kilowatt-hours— flowing into the ERCOT system

6.3.2	Basic Default Metering Function

The EPS Meter’s program shall be stored in non-volatile memory.

6.3.3	Data Recording Function

EPS Meters shall have the following interval data recording functions:

(a)	Provide recording of interval data for a minimum of four channels;

(b)

Use a “wraparound” memory that stores new interval data by writing over the oldest interval data;

(c)	Interval data shall be stored for a minimum of 45 days of four channel, 15-minute interval data, in addition to allowances for event recording (power outages, resets, time sets, etc.);

(d)	The recording of interval data function shall have the capacity to count and store at least 4,000 counts in a 15-minute period of time; and

(e)	Recording of interval data shall continue while the meter is communicating through any communications port.

6.3.4	Functions during Power Outage to Meter Power Supply

Meters shall have the following functions during power outage to the meter power supply:

(a)	During outage conditions the meter shall maintain all meter data as well as time keeping functions.  Display and communication functions are not required during these conditions;

(b)	The meter shall withstand the following outages without the need to maintain its power supply including replacing the battery:

(i)	Twenty short outages per year of less than 30 seconds per outage; and

(ii)	Thirty days of continuous/cumulative outage;

(c)	During a power outage, critical program and billing data shall be written to non-volatile memory.  When power is restored, data shall be returned to active memory and data collection resumed;

(d)	Upon restoration of power after an outage, the meter shall resume normal calculation of consumption and demand quantities.  Optional outputs shall also resume normal function.

(e)	During power outages, time shall be maintained with a cumulative error of no more than two minutes per week (0.02%);

(f)	The meter shall record the date and time of any power outage; and may also record the duration of any power outage.

6.3.6	Meter Test Mode Function

Meters shall have the following meter “test mode” functions:

(a)	The meter shall have the capability of a “test mode” function that suspends normal metering operation during testing so that additional consumption and demand from the tests are not added to the meter’s totals.  This includes the normal mode display registers and the interval data.  This requirement is imposed to prevent the test data from being recorded as actual load/generation data.

(b)	Security shall be provided to prevent unauthorized access to the “test mode”.

(c)	Activation of the test mode shall cause all present critical billing data to be stored in non-volatile memory and restored at the time of exit from the “test mode”.

(d)	The meter shall be programmed to automatically exit the “test mode” and return to normal operation after one hour or less of operator inactivity.

6.4	Consumption and Recording Requirements

6.4.1

Constants and Compensation Values

(1)	The meter shall be programmable to account for radial line losses and power transformer loss compensation as needed.

(2)	The meter shall be programmable to display and record the compensated values.  The values will be programmable in kWh, kVARh, etc.

6.4.2	Identifiers

The meter shall have a unique identifier for the MDAS ID.  The MDAS ID shall be capable of at least seven alphanumeric characters and shall be programmed internal to the meter.

6.5	Meter Diagnostics

6.5.1	Self-test Frequency

The meter shall be capable of performing a self-test.  At a minimum, the self-test shall be performed at the following times:

(a)	Whenever communications are established to the meter;

(b)	After a power-up; and

(c)	Once per day.

6.5.2	Self-test Checks

Upon failure of a self-test, the meter shall store an event log to be retrieved by the TDSP and/or ERCOT MDAS.  At a minimum, the following checks shall be performed during a self-test:

(a)	Check the backup battery usage or voltage;

(b)	Verify the program integrity; and

(c)	Verify the memory integrity.

6.5.3	Pulse Overrun

The meter shall be capable of detecting and reporting to the TDSP and/or ERCOT MDAS if the maximum pulses per interval have been exceeded during an interval.

6.5.4	Event Logging

(1)	When interrogated by ERCOT MDAS, meters shall be capable of logging and reporting the following events:

  - Hardware errors,

  - Firmware errors,

  - RAM and ROM errors,

  - Pulse Overflow errors,

  - Low battery condition,

  - AC power up,

  - AC power down,

  - Configuration changed,

  - Clock set/change,

  - Test mode activation, and

  - Inactive potential.

(2)	Definitions:

(a)	Hardware Errors: Various hardware malfunctions (i.e. Modem card/chip, measurement chip, CPU, etc.), whether fatal or not.

(b)	Firmware Errors: Firmware has a checksum error, watchdog time out error, or other problem with the firmware, whether fatal or not.

(c)	RAM and ROM Errors: Bad spots in memory identified via checksum or other means.

(d)	Pulse Overflow Errors: The maximum size value for the number of pulses per interval in load profile has been exceeded.  This does not apply to meters that store/report data in engineering units.

(e)	Low Battery Condition: Low battery has been sensed during initial power up, daily self checks, after power outages, or any other means to check for a low battery condition.

(f)	AC Power UP: When the meter electronics are powered up either via auxiliary power or connected to system power.

(g)	AC Power Down: When the meter electronics loses power either by auxiliary power or connected to system power.

(h)	Configuration Changed: Meter has been reprogrammed, or any meter programming where a settlement metering parameter is changed.

(i)	Clock Set/Change: The meter real time clock has been set/changed by external sources.

(j)	Test Mode Activation: Meter going into and out of “test mode”.

(k)	Inactive Potential: System phase voltage has been lost on any phase.

6.5.5	Error Reset

Fatal error or warning conditions shall only be reset upon an explicit command invoked via the meter programmer or upon some other explicit action by the TDSP EPS meter inspector.

6.6	Communication

6.6.1	Local Communications Interface

The meter shall be capable of communicating with a handheld reader or personal computer through a local port.

6.6.2	Internal/External Modem

Internal or external modems shall be capable of telephone communications at baud rates at a minimum of 1,200 baud.  The ring detect circuitry shall not be affected by transient voltage rises in the telephone line.

6.7	Accuracy Standards

6.7.1	Accuracy Class

EPS Meters shall meet or exceed the accuracy specifications contained in ANSI C12.20, 0.2 Accuracy Class.

6.7.2	Test Equipment

Meter accuracy and calibration tests, both shop and field, shall require only standard test equipment traceable to the National Institute of Standards and Technology (NIST).  No special laboratory-type test equipment or test procedures shall be required to assure the accuracy of the meter.

6.7.3	Start-up Delay

The meter shall start to calculate consumption and demand quantities within 15 seconds after power application to the metering electronics.

6.8	Electrical Requirements

6.8.1	Meter Forms, Voltage Ratings and Classes

EPS Meters shall be an approved ANSI form and comply with applicable ANSI C12 standards.  Two and one-half element meters shall not be used as EPS Meters.  The meter shall be TDSP approved Class 2, Class 10, or Class 20.

6.8.2

Clock

The meter’s internal clock shall be accurate within two minutes per week (0.02%) when not synchronized to the ERCOT system line frequency and shall be re-settable through the ERCOT communications interface.

6.9	Meter Package

The meter package shall comply with ANSI C12.10 requirements where applicable.  Switchboard/panel-board meters shall be in accordance with applicable NESC standards and must be mounted indoors or in an enclosure that meets all applicable NEMA standards.

6.10	Meter Password

The meter shall be programmable with a minimum of two unique passwords one being a read only password, to prevent unauthorized tampering by use of the optical port or the modem.  Passwords must be a minimum of four alphanumeric characters.  Access rights and capabilities shall be individually programmable for each password.

6.11	Data Security and Performance

No error, lockup or loss of data shall occur as a result of the following events:

(a)	Power outages, frequency changes, transients, harmonics, reprogramming (except re-initialization), time sync, or any meter communications;

(b)	Environmental factors—e.g. dampness, heat, cold, vibration, or dust; and

(c)	Multiple communication requests from different sources.

6.12	EPS Meter Approval

6.12.1	General Requirement

This subsection outlines the required testing a meter manufacturer must perform to assure the quality of EPS Meters.

(a)	All meters shall be in compliance with the latest revision of ANSI C12.20 at the 0.2 Accuracy Class, ANSI C12.1 and other ANSI C12 standards.

(b)

Any applicable tests required ensuring such meter meets the requirements specified in the SMOG and Protocol Section 10, Metering.

6.12.3	TDSP EPS Meter Conformance Requirements

(1)	TDSPs retain the responsibility for assuring the accuracy, integrity and MDAS compatibility of EPS Meters.  This subsection outlines the minimum TDSP requirements to ensure EPS Meters conform to the SMOG and the Protocols.  TDSPs may develop additional acceptance criteria with respect to EPS Meter selection without the approval of ERCOT.

(2)	Each TDSP shall maintain the following documentation for all meters they approve for use on EPS installations.

(a)	List of all meter manufacturer(s) and type(s) used; including:

(i)	Firmware version – date deployed and date discontinued including reason for discontinuation.

(ii)	Software version - date deployed and date discontinued including reason for discontinuation.

(b)	Manufacturer’s letter certifying compliance with applicable industry standards ANSI, the SMOG and applicable sections of ERCOT Protocols.

(c)	Manufacturer’s documentation detailing testing certification to the applicable industry standard ANSI, compliance with the SMOG and applicable sections of ERCOT Protocols.

(d)	Drawing(s) showing external meter connections.

(e)	Manufacturer’s instruction booklets detailing the necessary procedures and precautions for installation of the meter by field personnel including a step-by-step outline.

(f)	Manufacturer’s technical/maintenance manual for each meter style.  The manuals shall be sufficiently detailed so that circuit operation can be understood.

(g)	Software and associated documentation for the following:

(i)	Programming

(ii)	Diagnostics

(iii)	Data retrieval (meter reading)

(3)	Each TDSP shall ensure that the ERCOT MDAS can successfully communicate with any meter the TDSP approves for EPS use.

6.12.4

Changes to an approved EPS Meter

(1)	Meter manufacturers shall notify the TDSP of any changes to an approved meter that may affect such meter’s compliance with this attachment.

(a)	Meter manufacturers shall document and provide information to the TDSP on manufacturer firmware changes or updates for such meter.  Such information shall include the implementation date of such changes and the specific effects of such changes.  Such changes should be documented by meter serial number. Notification of such changes shall be provided in a timely manner.

(b)	Meter manufacturers shall document and provide information to the TDSP on manufacturer design changes for such meter.  Such information shall include the implementation date of such changes and the specific effects of such changes.  Such changes should be documented by meter serial number.  Notification of such changes shall be provided in a timely manner.

(2)	The TDSP shall evaluate such manufacturer changes to ensure the compliance to the Protocols and the SMOG before using such changed meter as an EPS Meter. The TDSP shall notify ERCOT in writing of any such changed meter that did not pass the compliance evaluation and fully explain the reason the meter did not pass.

(3)	The TDSP shall notify ERCOT in writing of any EPS Meter identified with a problem by the TDSP or the meter manufacturer. This notification shall include:

(a)	The identified problem.

(b)	Meter serial number.

(c)	The process the TDSP intends to implement to correct the problem(s).

(d)	A proposed timeline for problem resolution.

(e)	The estimated effect on meter accuracy for the time period the meter was and will be used to provide settlement data.

6.12.5	ERCOT Role regarding EPS Meters

(1)	ERCOT shall rely upon the TDSP for approval, verification, documentation and certification of EPS Meters.  However, ERCOT shall have the right to request compliance and certification documentation from meter manufacturers (for confidential material) and the TDSPs.

(2)	ERCOT shall notify TDSPs of EPS Meter problems disclosed to ERCOT as a result of TDSP product change evaluation or EPS Meter failure.

(3)	ERCOT shall assist the TDSP to ensure that MDAS successfully communicates with the EPS Meter being tested for approval.

Section 7:

General Specifications for Instrument Transformers for EPS Metering

7.1	Purpose

This Section specifies the technical requirements for Current Transformers (CT), and Voltage Transformers (VT) to be used for EPS metering Facilities.

7.2	Application

This Section applies to the following:

(a)	Single-Phase CTs;

(b)	Single-Phase VTs;

(c)	Single-Phase Combination Current/Voltage Transformers;

(d)	Coupling Capacitor Voltage Transformers; and

(e)	Fiber Optic CTs.

7.3	Standards

All instrument transformers covered by this Section shall be designed, manufactured, tested and supplied in accordance with the applicable ANSI /IEEE Standards and as required by the ERCOT Protocols and this Attachment.

7.4	Definitions

Refer to the latest edition of the Edison Electric Institute Handbook for Electricity Metering and ERCOT Protocol Section 2, Definitions and Acronyms.

7.5	Specifications

7.5.1	General

All instrument transformers covered by this Section shall meet the minimum BIL Rating as specified in ANSI C12.11 or IEEE standard C57.13-1993 Table 2 appropriate for the designated nominal System voltage or the latest ANSI Standard.

7.5.2	Nameplate Data

Instrument transformers shall be provided with a nameplate that lists the following but not limited to: manufacturer's name, type of device, serial number, ratios, burden, accuracy class, thermal rating factor, and impulse level.

7.5.3	Current Transformers

Current Transformers shall be either wire wound or a fiber optic system, which includes:  the physical unit, the optical sensor, the fiber optic cable, and optical conversion electronics.

7.5.3.1	Current Transformer Windings

Current Transformer windings (typical configurations) shall be either:

(a)	Single primary winding and single secondary winding with single or multi ratio tap(s);

(b)	Dual primary winding and a single ratio tap;

(c)	Single primary winding and one or more secondary windings with single or multi ratio tap(s); or

(d)

Other combinations as available and approved by ERCOT.

7.5.3.2	Rated primary current

The rating selected for primary current must be as specified by the TDSP based on supplied information.

7.5.3.3	Rated secondary current (Wire Wound)

The rated secondary current must be five amperes @ rated primary current.

7.5.3.4	Rated output (Fiber Optic System)

The output of the electronics in the fiber optic control unit shall be converted to one ampere @ rated primary current and used with an approved “class 2” style meter.

7.5.3.5	Accuracy (Wire Wound)

All current transformers shall have an accuracy of:

(a)	Standard – 0.3% accuracy class; or

(b)	Optional – 0.15 % accuracy class.

7.5.3.6	Accuracy and Burden (Fiber Optic System)

All fiber optic CT metering systems shall have an accuracy and burden of

0.3% accuracy class, ensuring that fiber connection is maintained within manufacturer’s prescribed limits. (This recognizes that optical units have an accuracy range closer to 0.15% from 5% to nominal current rating.)  Connected burden shall not exceed the burden rating of the system.

7.5.3.7	Continuous current rating factor

All current transformers shall meet or exceed a continuous current rating factor of:

(a)	Standard – 1.5 @ 30 degrees C Ambient; or

(b)	Optional – 1.0 @ 30 degrees C Ambient.

7.5.3.8	Short time thermal current rating

The short time thermal current rating shall meet the standards defined in IEEE Standard C57.13 – 1993 or the latest C57.13 Standard.

7.5.3.9	Mechanical short time current rating

The mechanical short time current rating shall meet the standards defined in IEEE Standard C57.13 – 1993 or the latest C57.13 Standard.

7.5.4		Voltage Transformers

7.5.4.1	Transformer windings

Transformer windings shall consist of a single primary winding and one or more tapped secondary windings.

7.5.4.2	Rated primary voltage

Rated primary voltage will be specified by the TDSP.

7.5.4.3	Rated secondary voltage

Rated secondary voltage will typically be 115/69 volts.

7.5.4.4	Accuracy

All voltage transformers shall have accuracy of:

(a)	Standard – 0.3% accuracy class; or

(b)	Optional – 0.15% accuracy class.

7.5.4.5	Thermal burden rating

The thermal burden rating of voltage transformers shall meet the standards defined in IEEE Standard C57.13– 1993 or the latest C57.13 Standard

7.5.5	Combination Current/Voltage Transformers (Metering Units)

Combination current/voltage transformers shall maintain the same electrical, accuracy and mechanical characteristics as individual CTs and VTs.  Physical dimensions may vary according to design.

7.5.6		Insulating Oil (if present)

Non-polychlorinated biphenyls (Non-PCB) insulating oil shall be used in oil filled instrument transformers.  The transformer shall be equipped with a non-corroding nameplate that indicates the dielectric fluid is non-PCB.

7.6	Testing

(1)	The TDSP shall ensure that each transformer is subjected to testing as prescribed by IEEE C57.13 - 1993 Standard or the latest C57.13 Standard.

(2)	The accuracy test results shall be submitted to ERCOT as outlined in Section 3, Documentation for EPS Metering Facilities.

Section 8:

Transformer and Line Loss Compensation Factors

  - Introduction

(1)	Transformer and line loss compensation refers to the practice of metering electrical energy delivered at a high-voltage billing point using metering equipment connected on the low-voltage side of the delivery point.  The metering equipment is provided with a means of correction that adds to, or subtracts from, the actual active and reactive metered values in proportion to losses that are occurring in the transformer and lines.

(2)	ERCOT approval is required for loss compensation performed in MDAS.  For a specific site, where a TDSP is requesting ERCOT to perform loss compensation in MDAS, the TDSP shall submit to ERCOT, for approval, a single percent loss correction value and supporting documentation verifying such value. Such loss compensation percentage values and supporting documentation shall be resubmitted to ERCOT on an annual basis or upon circuit parameter changes.

(3)	Transformer losses are divided into two parts:

- The core or iron loss (referred to as the no-load loss); and

- The copper loss (referred to as the load loss).

(i)	Both the no-load loss and the load loss are further divided into Watt and Var components.

(ii)	The no-load (iron) loss is composed mostly of eddy current and hystersis losses in the core.  No-load loss varies in proportion to applied voltage and is present with or without load applied.  Dielectric losses and copper loss due to exciting current are also present, but are generally small enough to be neglected.

(iii)	The load (copper) watt loss (I2 + stray loss) is primarily due to the resistance of conductors and essentially varies as the square of the load current.  The Var component of transformer load loss is caused by the leakage reactance between windings and varies as the square of the load current.

(iv)	Line losses are considered to be resistive and have I2R losses.  The lengths, spacings and configurations of lines are usually such that inductive and capacitive effects can be ignored. If line losses are to be compensated, they are included as part of the load losses (Watts copper).

  - Calculating Transformer Loss Constants

(1)	Transformer Loss compensation calculations with electronic meters are accomplished internally with firmware.  Various setting information and test data is required to program the meter.  The following information is required regarding meter installations:

- Transformer high voltage (HV) rating;

- Transformer kVa rating;

- Transformer high voltage (HV) tap settings;

- Transformer low voltage (LV) tap settings;

- Transformer connection (wye or delta);

- Transformer phases (1 or 3);

- Voltage transformer (VT) ratio;

- Current transformer (CT) ratio;

- Number of meter elements;

- Meter class; and

- Meter volts.

(2)	The following data is required from a transformer test report:

- (a)	No-load (iron) loss;

- (b)	Full-load (copper) loss;

- (c)	Percent impedance; and

- (d)	Percent excitation current.

(3)

The test data required may be obtained from the following sources:

- The manufacturer’s test report; or

- A test completed by a utility or independent electrical testing company

- 8.3	Transformer Load Tap Changer

(1)	Transformers equipped with a load tap changer (i.e., which has the capability to change transformer voltage tap positions or settings under Load) for regulating voltage, must have the loss compensation calculated at the median tap voltage.

(2)	When calculating the compensation for Auto-transformers that are in the TDSP rate base:

(a)	Iron losses will be part of system losses; and

(b)	Copper losses for the tertiary winding will need to be calculated to the highest voltage winding

(3)	All meters shall have their loss compensation calculations based on the methodology used in the 9th edition of the EEI Handbook for Electricity Metering.

  - Calculating Line Loss Constants

(1)	Line Loss compensation calculations with electronic meters are accomplished internally with firmware. Various information about the radial line is required to calculate the value which is programmed into the meter. It is not practical to compensate for line losses in a network connected line, only radial lines.

(2)	The following information is required about the line:

- Line type,

- Ohms per mile, and

- Length in miles of each type of line.

- 8.4.1	Switched Lines

Line Loss compensation for radial lines, which are switched, must be based on a negotiated average resistance based on the typical operating characteristics.

- 8.4.2

- Joint Use Facilities

In the case of joint use facilities (where facilities are used to deliver power to more than one entity) a fixed factor for losses is calculated based on the facilities’ peak load.  Such fixed factor shall be applied to the energy measured by each meter.

  - Reference Materials

The following additional references may be referred to for assistance when calculating the compensation factors referred to in this Section.

- (a)	Handbook For Electricity Metering, Edison Electric Institute, Ninth Edition, 1992.

- (b)	IEEE Std. C57.12.00-2000 “IEEE Standard General Requirements for Liquid Immersed Distribution, Power and Regulating Transformer”.

- Attachment

TRANSFORMER AND LINE LOSS COMPENSATION EXAMPLE

Name:

Delivery:

Location:

Rev. Date:

| HV Rated Voltage: | V | VT Ratio: | :1 |
| --- | --- | --- | --- |
| HV Tap: | V | CT Ratio: | :5 |
| LV Tap: | V | Joint Use (Y/N): |  |
| Trf. Conn. (Y/D): |  | Metering Trf. Use: | 100 % |
| Trf. Phase (1 or 3) |  | Contract kW: | kW |
| # Meter Elem.: |  | Power Factor: | % |

Comments:

TRANSFORMER DATA

| Serial Number | KVa Rating | No Load (Fe) Loss | Load (Cu) Loss | (Z) Impedance | (IE) Exciting Current |
| --- | --- | --- | --- | --- | --- |

| Total kVa rating: | Max Available kVa: |
| --- | --- |

LINE DATA

|  | Resistance | Length |
| --- | --- | --- |
| #1 Line Type: | Ohms/mile | Miles |
| #2 Line Type: | Ohms/mile | Miles |
| #3 Line Type: | Ohms/mile | Miles |
| #4 Line Type: | Ohms/mile | Miles |
| #5 Line Type: | Ohms/mile | Miles |
| #6 Line Type: | Ohms/mile | Miles |

**TRANSFORMER LOSS COMPENSATION TEST POINTS FOR WATTHOURS**

SERIES TEST

| Test Load | % Total |
| --- | --- |
| Full |  |
| 0.5 P.F. |  |
| Light |  |

**TRANSFORMER LOSS COMPENSATION TEST POINTS FOR VARHOURS**

SERIES TEST

| Test Load | % Total |
| --- | --- |
| Full |  |
| Light |  |

| Example: Transformer and Line Loss Compensation Calculation Sheet |  |  |  |  |  |  |  |  |  |  |  |  |  |
| --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- | --- |
|  |  |  |  |  |  |  | Date: 12/14/2000 |  |  |  |  |  |  |
| Transformer Information |  |  |  |  |  | Transmission Line Information |  |  |  |  |  | Meter Information |  |
| Xfmr Manufacturer |  | ABB |  |  |  | Line Type |  | 4/0 ACSR |  |  |  | PTR (xxx/1) | 60 |
| Xfmr Serial Number |  | 1000001 |  |  |  | Line Length (miles) |  | 7.360 |  |  |  | CTR (xxx/1) | 120 |
| Xfmr size (KVA) |  | 12000 |  |  |  | Line Res. @ 50 C |  | 0.592 |  |  |  | Meter Rated volt (v) | 120 |
| Xfrm Pri. test volt (p-p-v) |  | 110000 |  |  |  | *Total Line Res. |  | 4.357 |  |  |  | Meter class (amp) | 20 |
| Xfmr. sec. test volt (p-p-v) |  | 13090 |  |  |  | *Line Loss (VA) |  | 266549 |  |  |  | Number of elements | 3 |
| Xfmr. No-Load loss (Watts) |  | 22200 |  |  |  |  |  |  |  |  |  | *Meter Nominal Watts (watts) | 3600 |
| Xfmr. Excitation Current (%) |  | 0.45 |  |  |  |  |  |  |  |  |  | *Nominal CT Primary amp (A) | 1200 |
| Xfmr. Load loss (Watts) |  | 51360 |  |  |  |  |  |  |  |  |  | * Meter secondary test volt (v) | 125.9586 |
| Xfmr Impedance (%) |  | 8.84 |  |  |  |  |  |  |  |  |  | *Nominal Primary VA (VA) | 25920000 |
| *Xrmr sec. Test amp (A) |  | 529.27 |  |  |  |  |  |  |  |  |  |  |  |
| *Xfmr Pri Amps @ 1/2 Mtr Cl (A) |  | 142.80 |  |  |  |  |  |  |  |  |  |  |  |
| Loss Constants |  |  |  |  |  |  |  |  |  |  |  |  |  |
| *No Load VA loss (VA) |  |  |  |  |  |  |  |  |  | 54000 |  |  |  |
| *No Load loss phase angle (alpha) |  |  |  |  |  |  |  |  |  | 65.73 |  |  |  |
| *No Load Var loss (Var) |  |  |  |  |  |  |  |  |  | 49226 |  |  |  |
| *Load VA loss (VA) |  |  |  |  |  |  |  |  |  | 1060800 |  |  |  |
| *Load loss phase angle (beta) |  |  |  |  |  |  |  |  |  | 87.22 |  |  |  |
| *Load Var loss (Var) |  |  |  |  |  |  |  |  |  | 1059556 |  |  |  |
| % Transformer Losses |  |  |  | % Transmission Line Losses |  |  |  |  |  |  |  | % Total Losses |  |
| % Xfmr Watt Fe Loss | 0.07774 |  |  |  |  |  |  |  |  |  |  | %Tot. Watt Fe Loss | 0.07774 |
| % Xfmr Watt Cu Loss | 1.01857 |  |  | % Line Watt Cu Loss |  |  |  |  | 1.02835 |  |  | %Tot. Watt Cu Loss | 2.04692 |
| % Xfmr Var Fe Loss | 0.15645 |  |  |  |  |  |  |  |  |  |  | %Tot. Var Fe Loss | 0.15645 |
| % Xfmr Var Cu Loss | 21.01307 |  |  |  |  |  |  |  |  |  |  | %Tot. Var Cu Loss | 21.01307 |

| *Calculated values for the Transformer and Line Loss Compensation Calculation Sheet |  |
| --- | --- |
| Where: | Xfmr Sec. test amps=(Xfmr rating in VA)/(Xfmr secondary test p-p volt x Sqrt 3) |
|  | Xfmr Pri. Amp @ 1/2Mtr CL=(Xfmr Secondary test p-p volt/Xfmr Primary test p-p volt) x Nominal CT Primary Amp |
|  | Total Line Res.=Line Length x Line Res. (per mile) |
|  | Line Loss=3 x Total Line Res. x (Xfmr Primary Amp @ 1/2 Meter Class amp)^2 |
|  | Meter Nominal Watts=(Meter Class amp/2) x Meter Rated voltage x Number of elements |
|  | Nominal CT Primary Amps=(Meter Class amp/2) x CTR |
|  | Meter secondary test Volt=(Xfmr sec test volt)/(PTR x Sqrt 3) for 3 elm; (Xfmr sec test volt)/(PTR) for 2 elm |
|  | Nominal Primary VA=CTR x PTR x Meter Nominal Watts |
|  | No Load VA loss=(Xfmr Excitation current x Xfmr rating in VA) / 100 |
|  | No Load loss phase angle=acos(Xfmr No Load watts loss/No Load VA loss) |
|  | No Load Var Loss=No Load VA loss x sin(No Load loss phase angle (alpha)) |
|  | Load VA loss=(Xfmr Impedance x Xfmr rating in VA ) / 100 |
|  | Load loss ph angle (beta)=acos(Xfmr load loss/Load VA loss) |
|  | Load Var loss=Load VA loss x sin(Load loss phase angle (beta) |
|  | % Watt Fe Loss=((Xfmr No-load loss x (Meter rated volt/Meter sec. test volt)^2) / Nominal Primary VA) x 100 |
|  | % Watt Cu Loss=((Xfmr Load loss x ((Meter Class amp/2) x (CTR/Xfmr sec. test amp))^2) / Nominal Primary VA) x 100 |
|  | % Var Fe Loss=((No Load Var loss x (Meter Rated volt/Meter Sec. test volt)^4) / Nominal Primary VA) x 100 |
|  | % Var Cu Loss=((Load Var loss x ((Meter Class amp/2) x (CTR/Xfmr sec. test amp))^2) / Nominal Primary VA) x 100 |
|  | % Line Cu Loss=(Line Loss VA/ Nominal Primary VA) x 100 |
|  | % Total Losses= %Xfmr(Fe or Cu) losses + %Line(Fe or Cu) losses |

| Percent Error Calculations for meters |  |  |
| --- | --- | --- |
| With Transformer/Line Loss Compensation |  |  |
| FL = 120 VOLTS @ 5 AMPS @ UNITY | FL= | 1.179 |
| LL = 120 VOLTS @ .5 AMPS @ UNITY | LL= | 1.657 |
| PF = 120 VOLTS @ 5 AMPS @ 50% | PF= | 2.358 |
| Calculations for Watt Loss Compensation |  |  |
| FL = 1/2 Watt CU losses + 2 * Watt FE losses |  |  |
| LL = 1/20th Watt CU losses + 20 * Watt FE losses |  |  |
| PF = UNITY * 2 |  |  |

Section 9:

Data Validation, Estimation and Editing Procedures

9.1

ERCOT Validation Process

Refer to Protocol Section 11, Data Acquisition and Aggregation, for the ERCOT validation process.

9.2	ERCOT Editing and Estimation Process

(1)	In the event ERCOT cannot communicate with the primary and back-up EPS Meters through the normal communications path, either of the following should be utilized if possible:

- (a)	Temporary Alternate Communications (Cell Phone, Microwave, Satellite, and any other ERCOT MDAS compatible communications), or

- (b)	Compatible ERCOT MDAS Formats (MV-90 “p” files, HHF, etc.).

(2)	Once it has been determined that data cannot be retrieved from the EPS Meters, ERCOT will perform an estimate utilizing the best available data and sound engineering practices.

The following are examples of data that may be used:

- (a)	Non-EPS Meter data; and

- (b)	SCADA data in conjunction with data provided by the Resource Entity.

9.2.1

Examples

# (1)	Blown CT --

# It was determined that data gathered from a metering point was incorrect due to a failure to a CT.  This means that the data retrieved by the ERCOT MDAS is understating the actual quantity generated/consumed at the metering point.  ERCOT determines from test reports that the energy flow is typically balanced across all phases.  Since the meter is only recording data based on two working CT’s, the data would be increased by a factor of 1.5 (Metered value is 66% of actual) to adjust for the CT failure.

Example: Actual generation value equals: 30 MWH.

Actual metered value equals: 30 MWH * 0.66666666 = 20 MWH

Estimated value equals: 20 MWH * 1.5 = 30 MWH

- (2)	Determine un-metered generation using meter data --

- A generation site consisting of three units has an EPS Meter installed on each unit.  For one of the units, the primary and backup meters are destroyed due to lightning.  ERCOT determines that another non-EPS Meter is available for the whole site (i.e. the meter includes all the generation from the three units).  To determine an estimate of the missing unit’s generation, ERCOT would take the non-revenue quality total site meter and subtract the two EPS Meter values from the two other generation units.

# (3)	Determine un-metered generation using SCADA data --

# A site consisting of three generation units has EPS Meters installed at the transmission point of interconnect.  The primary and backup meters are destroyed due to lightning.  The SCADA signals from all three units were unaffected.  ERCOT will retrieve and sum the signals for a like period when EPS Meter data was available.  ERCOT will then perform a comparison analysis to compute an adjustment factor that will be applied to the SCADA data.

Example: SCADA signal for like period per unit is 10MWH.

Total for the 3 units is 30 MWH.

Actual metered value for like period equals 26 MWH

Adjustment factor equals 26/30 = .866667

SCADA signal for estimate period equals 35MWH

Estimated value equals: .866667 * 35 = 30.333333

Technical Metering Attachment G:

change control Processes

ERCOT Market Rules is revising the change control process for these guides. This section will be updated through the change process when these revisions are complete.

- Settlement Metering Operating Guides (SMOG)

- Overview

The following process has been established to announce, develop, revise, and approve changes to the Settlement Metering Operating Guides (SMOG):

- Proposed SMOG revisions are submitted to ERCOT at epsmetering@ercot.com.

- The Metering Working Group (MWG) reviews the Settlement Metering Operating Guides Revision Request (SMOGRR) and recommends an action to the Wholesale Market Subcommittee (WMS).

- After reviewing the MWG’s recommendation to revise the SMOG, the WMS approves or rejects the recommendation.

- If approved, the WMS submits proposed SMOG language revisions to the Technical Advisory Committee (TAC) for review and approval.

- The TAC reports the results of all TAC votes regarding proposed SMOG revisions to the ERCOT Board of Directors.

- Throughout the SMOG, references are made to the Protocols.  Protocols are subject to their own revision process, not this SMOG revision process.

- Roles and Responsibilities

- Market Participant

Any Market Participant may submit a SMOGRR. The Market Participant is responsible for monitoring the progress of their submittal. Submitters are encouraged to attend MWG meetings and offer suggested language that ensures the intent of the request is maintained.

- MWG

- The MWG has ultimate responsibility for ensuring that the SMOG are compliant with Protocols.  As such, the MWG will monitor all changes to Protocols and initiate any SMOGRRs necessary to bring the SMOG into conformity with Protocols.

- The MWG will acknowledge receipt of all SMOGRRs it receives.  The MWG will also provide progress updates to the submitter of the SMOGRR apprising the submitter of the status of the SMOGRR at each major step of the approval process.  All communication between the submitter of a SMOGRR and the MWG will be done using electronic mail.

- ERCOT

- When ERCOT is assigned duties in the Change Control Process the ERCOT Settlement Metering Department will be responsible for performing the work.

- ERCOT will have the responsibility for managing the database used to track submitted changes to the Settlement Metering Operating Guides.

- Step by Step Process

| CHANGE CONTROL PROCESS |  |
| --- | --- |
| STEP | PROCESS |
| - Request to Revise Settlement Metering Operating Guides | Requests to revise the SMOG are submitted electronically to ERCOT utilizing the designated SMOGRR form. Any entity with a legitimate interest in Settlement Metering may offer a pertinent revision for consideration. These entities include, but are not limited to: - Transmission and Distribution Service Providers - Competitive Retailers - Load Serving Entities - Power Marketers - Qualified Scheduling Entities - ERCOT Subcommittees, Task Forces, and Working Groups - ERCOT - Non Opt In Entities - PUCT Market Oversight Committee The original submission of a SMOGRR must be accompanied by a description of the requested revision, the reason for the suggested revision, a list of any other affected ERCOT Guides sections, and the suggested SMOG language. A SMOGRR is first submitted to ERCOT where the request is verified for completeness. Within five business days ERCOT will notify the submitter that the SMOGRR has been received. At this time ERCOT will also inform the submitter whether the SMOGRR is considered complete or not complete. Completed SMOGRRs are forwarded to the MWG for review. SMOGRRs that are not complete are returned to the submitter. No further action will be taken by ERCOT on any SMOGRR deemed incomplete. To pursue the request further, the submitter must submit a new SMOGRR. ERCOT will use the Metering Exploder list to forward the SMOGRR to the Chair of the MWG. The Chair will place this SMOGRR on the agenda for the next regularly scheduled MWG meeting. If the next regularly scheduled MWG meeting will occur more than 30 days after a SMOGRR is submitted to ERCOT, the Chair of the MWG may convene a special meeting of the MWG to discuss this request. |
| - Metering Working Group Reviews Request and Recommends Action | As part of the SMOGRR evaluation process, the MWG will establish a timetable for completing its review and analysis of the submitted SMOGRR. The MWG will provide a recommended implementation date for any SMOG language forwarded to the WMS for review and approval. The MWG will be responsible for verifying the accuracy of all information contained in a submitted SMOGRR. The MWG will also be responsible for researching the impacts to other Operating Guides when making this SMOG language revision. Further, the MWG will be responsible for ascertaining that the proposed SMOG language revision complies with Protocols. The MWG will sponsor changes to the Protocols when these changes must be made to accommodate the proposed SMOG language revisions. During the process of evaluating a SMOGRR, the MWG may circulate the proposal to other working groups for review and comment. The MWG shall have no responsibility to address or incorporate comments from the other working groups into its SMOG language revisions. After the MWG reviews the SMOGRR one of three actions will be taken: - The SMOGRR is accepted as submitted and the SMOG language revisions are forwarded to the WMS for approval, or - The SMOGRR is accepted with MWG modifications and the resulting SMOG language revisions are submitted to the WMS for approval, or - The SMOGRR is rejected. Action 1. When the MWG accepts a SMOGRR as submitted, the MWG will forward the proposed SMOG language revisions to the WMS for review and approval at the next regularly scheduled meeting of the WMS. Action 2. When the MWG accepts the SMOGRR in principle, but has concerns with some elements of the SMOGRR, the MWG will draft alternative proposed SMOG language. The revised SMOG language will be submitted to the WMS for review and approval at the next regularly scheduled meeting of the WMS. The MWG will inform the entity submitting the SMOGRR that the MWG will forward the SMOG language revisions to the WMS for review and approval; however the MWG has modified the submitter’s proposed SMOG language revisions to better reflect the viewpoint of the MWG. The submitter may forward its original SMOGRR to the WMS for consideration as an alternative to the SMOG language revisions submitted by the MWG. Action 3. When the MWG rejects a SMOGRR the MWG will issue a report to the submitter of the SMOGRR within five business days of the MWG making its determination. This report will include the original SMOGRR and a detailed reason for the rejection decision. A submitter has ten business days to register a request to appeal the decision of the MWG with the WMS. |
| - Wholesale Market Subcommittee Reviews and Comments on Recommendation to Revise Guides Language | When the WMS reviews the proposed SMOG language revisions one of four actions will be taken: - The proposed SMOG language revisions are approved as submitted, or - The proposed SMOG language revisions are conditionally approved for submittal to the TAC, or - The proposed SMOG language revisions are sent back to the MWG for further work, or - The proposed SMOG language revisions are rejected. Action 1. When the WMS approves the proposed SMOG language revisions as presented, the WMS will submit the proposed SMOG language revisions to TAC for review and approval. Action 2. When the WMS accepts the proposed SMOG language revisions, but requests the MWG make specific changes to the language before having it submitted to the TAC, the MWG could accept or reject the language edits offered by the WMS. If the MWG accepts the language edits offered by the WMS then the SMOG language revisions are forwarded to the TAC for review and approval. If the MWG rejects the language edits made by the WMS then SMOG language revisions are treated as though the WMS sent it back to the MWG for further work. Follow the steps for Action 3. Action 3. When the WMS accepts the proposed Guides language revisions in concept, but has concerns with some of the details, the WMS will return the proposed SMOG language revisions to the MWG with comments and a request for additional MWG work on this proposal. The MWG can take one of two further actions: - Discontinue further action toward implementing the proposed SMOG language revisions, or - Modify the proposed SMOG language revisions to accommodate concerns of the WMS. - Further Action 1. - When, after taking into consideration the review and commentary of the WMS, the MWG determines that the proposed Guides language is not necessary, a response will be prepared stating why the proposed Guides language revisions are no longer being pursued by the MWG. This response will be sent to the Chair of the WMS, and to the submitter of the original SMOGRR. - Further Action 2. After the proposed SMOG language revisions have been modified to accommodate concerns raised by the WMS, the Chair of the MWG will submit the modified proposed SMOG language revisions to the WMS for review and approval. Action 4. When the WMS decides not to approve the proposed language revisions, the WMS will provide the MWG with reasons why the WMS rejected the proposed SMOG language revisions. - At this point the MWG can pursue one of two further actions: Discontinue further action toward implementing the proposed SMOG language revisions, or - Resubmit the proposed SMOG language revisions to the WMS after reworking it to address the objections of the WMS. Further Action 1. When the MWG accepts the decision of the WMS, then a response to the submitter of the SMOGRR is prepared by the MWG stating that the MWG will take no further action concerning the SMOGRR. This communication will state that the WMS rejected the proposed SMOG language revisions suggested in the SMOGRR. This communication will also state the reasons why the WMS rejected the proposed SMOG language revisions. Further Action 2. When the MWG determines that the proposed SMOG language revisions should be adopted, the MWG will develop proposed SMOG language revisions that address the objections raised by the WMS during this Subcommittee’s initial review of the proposed SMOG language revisions. The revised SMOG language revisions will be resubmitted to the WMS for review at the next regularly scheduled meeting of the WMS. Step three of this process begins anew. |
| - Technical Advisory Committee Reviews the Proposed Guides Language Revisions | The TAC will review the proposed Guides Language revisions at its next regularly scheduled meeting where one of three actions will occur: - The proposed SMOG language revisions are approved as submitted, or - The proposed SMOG language revisions are sent back to the MWG for additional work. - The proposed SMOG language revisions are rejected. Action 1. If the TAC approves the proposed SMOG language revisions, the revisions will have an effective date occurring on the first day of the month following TAC approval unless otherwise designated by the MWG. Action 2. If the TAC determines that the proposed SMOG language revisions need further work, then the request will be sent back to the MWG to address TAC’s issues. Unless otherwise directed, the resulting modified SMOG language must pass through the WMS review and approval process described in Step 3 above. Action 3. If TAC rejects the proposed SMOG language revisions, the MWG will terminate any further activity toward implementing these proposed SMOG language revisions. Within three business days of TAC making its decision, the MWG will notify the entity submitting the SMOGRR of TAC’s decision to reject the proposed SMOG language revisions as suggested in the SMOGRR. |
| - Technical Advisory Committee notifies the ERCOT Board of all votes taken related to Guides Revisions | The Chair of TAC shall report the results of all votes by TAC related to the SMOG language revisions to the ERCOT Board at their next regularly scheduled meeting. |