## ERCOT Operations Report

## ROS & OWG

## November 2005

Frequency control   59.9 > F > 60.1

|  | Frequency |  |
| --- | --- | --- |
| 11/9/2005 7:14 | 59.826 | 3 unit train; 545 MW |
| 11/12/2005 10:05 | 59.883 | ERCOT SCE = -732. One QSE SCE = -320. Another QSE SCE = -220. 340 MW RRS deployed, Up Regulation at maximum of 740. |
| 11/17/2005 3:11 | 59.829 | 560 MW |
| 11/17/2005 17:18 | 59.824 | 770 MW |
| 11/18/2005 0:53 | 59.899 | 330 MW |
| 11/25/2005 10:06 | 60.131 | Offset miscalculated. 2 VDI issued to reduce generation 700 MW total. |
| 11/27/2005 23:04 | 60.131 | Resource Plan adjusted up 500 MW after Hour Ahead (HA) study had been ran. IE 23:15 HA study was completed at 22:38. Operating Period Desk Procedures require the study to be ran again if the Resource Plan changes more than 100 MW. Release 4 enhancements allow for the Resource Plan to be adjusted after the last study can be run. All of the 980 MW of available Up Regulation was exhausted during this event. |

Deployed Responsive (19) (Reported Above)

| 06:00 & 22:00 | 11/5/05 15:11:44 | 11/16/05 17:49:14 |
| --- | --- | --- |
|  | 11/5/05 23:16:20 | 11/17/05 3:11:02 |
| 11/1/05 6:08:20 | 11/8/05 2:09:56 | 11/17/05 17:18:06 |
| 11/3/05 6:08:20 | 11/9/05 7:14:02 | 11/18/05 0:53:48 |
| 11/30/05 6:09:24 | 11/12/05 10:02:32 | 11/21/05 5:05:06 |
| 11/7/05 22:00:16 | 11/12/05 11:05:26 | 11/29/05 19:58:58 |
| 11/29/05 22:06:44 | 11/15/05 0:07:22 | 11/30/05 15:50:06 |

Day Ahead Capacity Purchases

| Historical OOMC/RMR | Nov 04 | Oct 05 | Nov 05 |
| --- | --- | --- | --- |
| DFW | 7 | 42 | 8 |
| E RIO | 57 | 115 | 142 |
| W RIO | 29 | 36 | 39 |
| Laredo | 40 | 52 | 42 |
| Bryan Area | 6 | 54 | 29 |
| Corpus | 30 | 31 | 8 |
| South | 0 | 14 | 0 |
| North | 0 | 6 | 10 |
| Western | 0 | 7 | 7 |
| Houston | 0 | 41 | 3 |
| San Antonio | 0 | 8 | 61 |
| Northeast | 0 | 0 | 2 |
|  | 199 | 406 | 351 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overload | Days |
| --- | --- | --- |
| Dansby - Hearne 138kV | Hearn - Hearne Switch 69kV | 16 |
| Skyline - Marion - STP 345kV | Schertz - Parkway 138kV | 13 |
| Marion - Hill Country & Skyline 345kV | Schertz - Parkway 138kV | 10 |
| Gibbons Creek - Bryan East - Greens Prairie 138kV | Texas A&M - Dansby 138kV | 8 |
| Clear Spring & Marion - Zorn 345kV | Seguin - Zorn 138kV | 6 |
| Pawnee - Lon Hill 345kV | San Miguel - Sigmore 138kV | 3 |
| Stryker Creek - Trinidad 345kV | Athens N Sw - Athens Tap 138kV | 3 |
| Comanche Peak - Decordova & Wolf Hollow - Rocky Creek 345kV | Concord 345/138kV auto | 2 |
| Comanche Peak 1 & 2 | Uvalde - Asphalt Mines 138kV | 2 |
| Dilley Sw - North Laredo 138kV | Asherton - North Laredo 138kV | 2 |
| Duke #1 or #2 | Rio Hondo-MVEC/Burns | 2 |
| La Palma - Rio Hondo 345kV | Rio Hondo - Rio Hondo MV 138kV | 2 |
| La Palma - Rio Hondo 345kV | South McAllen - Hidalgo 69kV | 2 |
| Rio Hondo - La Palma 345kV | South McAllen - Las Milpas 138kV | 2 |
| Barrilla - Fort Stockton 138kV | Barrilla - Fort Stockton 69kV | 1 |
| Dilley Switch - San Miguel 138kV | Derby - Pearsall 69kV | 1 |
| Fisher Road Switch - Oklaunion & Bowman Switch 345kV | Vernon - Grayback 69kV | 1 |
| Graham - Benbrook & Parker Sw 345kV | Stephenville - Lingleville 138kV | 1 |
| Lon Hill - Coleto Creek 345kV | Lon Hill - Pawnee 345kV | 1 |
| Mesquite East-Forney 138kV | Forney Sw-Mesquite East 138kV | 1 |
| North Edinburg-Bates 138kV | North Edinburg-Moore Field 69kV | 1 |
| Pawnee - Lon Hill 345kV | Blessing - Lolita 138kV | 1 |
| Sandow #4 | Gideon-Butler 138kV | 1 |
| Sandow SES 345/138kV tr | Sandow - Salty 138kV | 1 |
| Sonora - Friend Ranch 138kV | Friend Ranch - Ozona 69kV | 1 |
| STP-Skyline-Hill Country 345kV | Zorn-Seguin 138kV | 1 |
| Temple Sw-Bell County 138kV | Seaton - Poag 69kV | 1 |
| Trinidad - Watermill - Tricorner 345kV | Forest Grove Switch - Mabank Tap | 1 |
| Westside CSW - Airline CSW 138kV | Port Aransas - Mustang Island 69kV | 1 |

| South to Houston | 6 |
| --- | --- |
| North to Houston | 3 |
| West - North | 1 |
| West to North | 1 |

New RAP

- None

- New Procedures/ Forms/Operations Bulletins

11/04	ERCOT Market Operations Bulletin 28  - Settlement implication of the revision to local balancing energy project.

11/09	ERCOT Power Operations Bulletin 224 – T&S desk procedures for using SCADA tags.

Blackout/Load Shed incidences and major system voltage problems

11/16 09:15	   Maintenance in the Dansby switchyard caused a breaker on the 138 kV bus to open, isolating the high side of the 138/69 kV transformer at Dansby.  Only local generation and the 138/69 kV transformer at Hearne fed the local 69kV system.  Low voltage was observed at stations including North Bryan, Tabor, Industrial Park, Shady Lane, East, Nall Lane, Atkins, and Dansby.  ERCOT dispatched local generation to full capacity to alleviate the loading of the Hearne transformer and the Boonville – Briarcrest 69kV line.  The transformer at Hearne loaded to 121.6% of its 60 MVA rating and the Boonville – Briarcrest 69kV line to 117% of its Normal 41 MVA rating.

Booneville – Briarcrest 69 kV line opened at 09:28, separating the local 69 kV system from ERCOT and mitigating the flow on the Hearne transformer.  All three stages of high-set under-frequency relays actuated and 22 MW of load was shed at North Bryan, Industrial Park, East, Nall Lane, and Briarcrest.

At 09:39, the Dansby 138kV breaker was reclosed which synchronized the 69kV island with ERCOT. By 09:53 the bulk of the load was restored. At 10:14 the last feeder was back in service restoring all load. At 10:57 the Boonsville – Briarcrest 69kV line was returned to service.

During the event, the following transmission outages were active:

Atkins 138/69 kV transformer

East 138/69 kV transformer

Atkins – Texas A&M Sw 138kV line

Dansby – Texas A&M Sw 138kV line

Texas A&M Sw – Texas A&M 138kV line

The contingency and overload had been observed as recently as 6:00 a.m. that morning, but was not observed prior to the event.

Voltage Instructions

11/3 22:30	2 stations received instructions to lower kV in South Zone.

11/4 23:30	 1 station received instructions to lower kV in South Zone.

11/8 16:30	 2 kV raise instruction in North Zone.

11/9 13:30	 2 kV raise instruction in North Zone.

11/9 14:30	 2 kV raise instruction in North Zone.

11/15 13:30	345 kV bus voltages in the Valley and at Lon Hill dropped roughly 10 kV over the previous hour.  Lon Hill voltage approached 330 kV.  Reactive support was requested from available generation over a wide area in the South Zone.

11/16 00:30	1 kV lower instruction in the South Zone.

11/17 23:45	2 stations received instructions to lower kV in South Zone.

11/21 12:00	1 kV lower instruction in the South Zone.

11/21 12:30	2 kV lower instruction in the South Zone.

11/24 12:00	2 kV lower instruction in the North Zone.

Corpus Christi RMR status summary

ERCOT has announced a need for a unit at Barney Davis for 2006.  Study results related to this decision are posted at the ERCOT Operations and System Planning data website under “Reliability Must-Run (RMR) Studies” folder ERCOTSempraRMRStudyFiles11152005.zip

Major Computer Problems, Enhancements & Fixes

None

Communication

None

ERCOT peak (Unofficial)

11/09	16:00 42,580

Alerts, OCN, and Emergency Notices

| November Transmission Alerts |  |  |
| --- | --- | --- |
| 11/7 | 14:30 - 22:00 | Loss of Pawnee to Lon Hill loads San Miguel to Sigmore. |
| 11/7 | 14:30 - 22:00 | Loss of San Miguel tr loads Derby to Pearsal. |
| 11/8 | 14:45 - 17:15 | Loss of Pawnee to Lon Hill loads San Miguel to Sigmore. |
| 11/8 | 14:45 - 17:15 | Loss of San Miguel tr loads Derby to Pearsal. |
| 11/10 | 16:00 - 17:50 | Loss of San Miguel tr loads Derby to Pearsal. |
| 11/11 | 15:00 - 19:30 | Loss of Pawnee to Lon Hill loads San Miguel to Sigmore. |
| 11/14 | 14:50 - 22:00 | Loss of Pharr - Pharr MVEC loads N Edinburgh - McColl Road |
| 11/14 | 14:50 - 22:00 | Loss of San Miguel tr loads Derby to Pearsal. |
| 11/15 | 10:15 -23:15 | Loss of San Miguel tr loads Derby to Pearsal. |
| 11/15 | 10:15 -24:00 | Loss of Ingleside CT loads Ingleside-Air Liquide |
| 11/16 | 0:15 - 2400 | Loss of Ingleside CT loads Ingleside-Air Liquide |
| 11/17 | 0:15 - 14:30 | Loss of Ingleside CT loads Ingleside-Air Liquide |
| 11/19 | 12:50 -17:38 | Loss of West Waco - North Temple or McGregor Phillips tr cause voltage violations at the Gatesville Switch, McGregor Phillips, McGregor TU, Waco Atco and West Waco stations on the 69kv system. |
| November Capacity OCN & Alerts |  |  |
| 11/23 | 12:15 - 13:45 | OCN - Insufficient capacity for HE 19:00. |
| 11/23 | 13:45 - 18:40 | Alert - Insufficient capacity for 19:00 & 20:00. |
| 11/27 | 00:15 - 01:30 | OCN - Insufficient capacity for HE 18,19,20 |
| 11/27 | 01:30 - 16:00 | Alert - Insufficient capacity for HE 18,19,20 |

Other

11/15 22:56 	Port Isabel – South Padre Island, Port Isabel – South Carbide, and South Carbide – Titan Tire 138kV lines tripped during storm conditions in the area. ~ 40 MW of load was lost at the Port Isabel, Causeway, South Padre Island, Sunchase, and Titan Tire stations. The lines were restored at 00:14 on 11/16/05, restoring the load lost.

At 01:07, the Port Isabel – South Padre Island, Port Isabel – South Carbide, and South Carbide – Titan Tire 138kV lines tripped again dropping the same load. By 01:45 all load and the Port Isabel – South Padre Island, and Port Isabel – South Carbide 138kV lines were restored. The South Carbide – Titan Tire 138kv was restored at 18:06 on 11/16/2005.

The Port Isabel – Causeway and the Port Isabel – La Palma 138kV lines were on planned clearances during the event.