## Sheet1
Section 3 Protocols Clarification |  |  |  | 0.001
Reviewer | Section | Requested Clarification | TPTF Mtg Action 12152005 | 0.002
Mark Patterson | 3.1.3.2 (1) & (2) | Should this section be specific to Generation Resources as opposed to all Resources? |  | 1 | 0.3
Ralph Poston | 3.1.4.4 3.1.6.5 | This is a change from current operating procedures. The rules established in PRR 425 gave priority to previously approved Transmission outages over proposed Resource outage scheduled less than 8 days prior planned start date. Was this an intended change needed for the Nodal Market? |  | 1 | 0.4
Lee Caylor /Curtis Crews | 3.1.5.3 3.3.2.1 (d) | Outages timelines do not correlate to NOMCR timelines. NOMCR requires outage information |  | 1 | 0.5
Ralph Poston | 3.1.5.9(b) | What are the predefined classifications? If they are not defined, who is responsible for the definitions? |  | 1 | 0.5
Lee Caylor /Curtis Crews | 3.5.1 (4) 3.5.1 (5) | Timing issues with the PRR Process versus the NOMCR Process. The possibility that the Hub definition in the Protocols will not match a Hub definition in various models will exist. |  | 5 | 0.1
Lee Caylor /Curtis Crews | 3.5.1 (5) 3.10 (5) 3.10 (9) 3.10.2 (1) | No requirements in 3.11 Transmission Planning. 3.10.2 (1) needs emphasized/repeated in 3.11 to clarify responsibilities. SSWG has already publicly declared that the Planning workflows currently in place will not change will Nodal implementation. |  | 5 | 0.1
Lee Caylor /Curtis Crews | 3.5.2.1 | Most of the North 345 kV Trading Hub (North 345) has SSWG Bus Numbers associated with definition. The rest of the Hubs do not. There are no rules applied for changing Bus Numbers. Bus Numbers can be re-used or changed by Market Participants. |  | 5 | 0.2
Lee Caylor /Curtis Crews | 3.5.2.1 (4) 3.5.2.2 (4) 3.5.2.3 (4) 3.5.2.4 (4) 3.5.2.6 (4) | "SECD" should be "SCED" in definition of RTHBP |  | 5 | 0.2
Lee Caylor /Curtis Crews | 3.5.2.1 (4) | Variable "Hb" not used. Possibly typo as "hb" |  | 5 | 0.2
Lee Caylor /Curtis Crews | 3.5.2.3 (1) | Appears to be some typo errors in Houston Hub bus list. |  | 5 | 0.2
Ted Hailu | 3.7(1) | This says QSEs must submit resource parameters. Today, Resource Entities submit them. Was this intentionally changed? |  | 7 | 0 | 1
Art Deller | 3.7.1.1(2) | Does "Resource" mean "Unit"? |  | 7 | 0.1
Trip Doggett | 3.8(6) | What does "all individual Split Generation Resources in a generation facility must be committed or decommitted together" mean? Does this mean RUC has to select all individual offers before committing the facility? |  | 8 | 0 | 6
Trip Doggett | 3.9.1 | Should there be a status for BLT? (See 6.5.9.5.2) |  | 9 | 1 | 0
Trip Doggett | 3.9.1 | Should there be a status for DC Ties? (See 4.4.3(8)) |  | 9 | 1 | 0
John Dumas | 3.9.2(7) | Current Operating Plan Validation "ERCOT systems must be able to detect a change in status of a Resource shown in the COP and must provide notice to ERCOT operators of changes that a QSE makes to its COP." Question – Does ERCOT track the change in status from the Day Ahead submission of the Resource or from the last HA submission? What is the point of reference? |  | 9 | 2 | 7
Doug Evans | 3.10(1) | How many network models will be placed in the MIS Secure Area? Do they represent different time periods? |  | 10 | 0 | 1
Jay Dondeti | 3.10(5) | Definition of the word "identical"? "For operational and planning models that are intended to represent the same system state the results sould be identical and the naming should be consistent." Does this mean the operations model and planning model, should both be represented in a common format like CIM. Does it also mean the planning study results must be specified in a format that allows the naming convention that is consistent with the operations model. For example electrical bus in PTI is a number vs in the operations model it could be an identifier. |  | 10 | 0 | 5
Lee Caylor /Curtis Crews | 3.10(7) | Current wording says ERCOT shall convert to be CIM compliant. Process should be that no NOMCRs will be accepted that are not CIM compliant |  | 10 | 0 | 7
Lee Caylor /Curtis Crews | 3.10(8) | "ERCOT shall post all NOMCRs on the MIS Secure Area within five Business Days following receipt of the NOMCR, consistent with CEII standards." Interpretation- ERCOT will post NOMCRs after all required data has been received. Incomplete NOMCRs will not be posted. |  | 10 | 0 | 8
Lee Caylor /Curtis Crews | 3.10(11) | "ERCOT shall approve or reject the request, including any revisions made by the requestor, within fifteen (15) days of receipt of the complete request and any revisions." Conflicts with Timeline in 3.10.1 (What happens to NOMCRs submitted on last day of month? Does 3.10 (10) apply here?) Determination of validity of data will prove to be difficult if vast quantities of data are provided on the last day (or near the end) of a deadline. ERCOT has no control over the amount of data submitted. |  | 10 | 0 | 11
Lee Caylor /Curtis Crews | 3.10.1(1) 3.10.3 (1) | CRR model updates and Network Operation Model updates are on different timelines and are utilized for different time periods (e.g. CR one and 2 year auction but NOMCR process (3.10.1 (1) ) indicates that updates "may" be submitted one year in advance of the timeline in 3.10.1 (3). |  | 10 | 0.1
Wagner | 3.10.1(5) | Requires consistent information "in the various models used by ERCOT Operaitons, ERCOT Planning, and other workgroups," such that models "intended to represent the same system state" yield "identical results." Is it possible, with the different designs of the models (bus vs. breaker) that a powerflow would yield the same results across both of the models. Do we want change the word "identical" to "comparable?" Name is also required to be consistent and an annual audit is required. Do we want specifications on what the audit should verify? |  | 10 | 0.1
Doug Evans | 3.10.2 | This will still require a collaborative effort with the TDSPs. The SSSWG and possibly the NDSWG members will need to be invovled. Will there still be a need for the on peak and off peak seasonal cases for the upcoming year? Do seasonal loss factors for the system and NOIEs still need to be calculated? Are there any new expectations for cases that would need to be developed for the Nodal Market? |  | 10 | 0.2
Lee Caylor /Curtis Crews | 3.10.2(4) | Clarify CRR timeframe requirement for the Planning model and relationship to 3.10.3 (4) |  | 10 | 0.2
Doug Evans | 3.10.3(1) | What are the timeframes for the models necessary for CCR auctions? |  | 10 | 0.3
Lee Caylor /Curtis Crews | 3.10.3(2) | No explicit requirements in 3.11 Transmission Planning or 3.10.2. Please clarify if the Planning Models should reflect requirements. |  | 10 | 0.3
Wagner | 3.10.3(3) | Requires the one line diagram for the CRR model to include all Settlements points "indicating the settlement point that the Electrical Bus is part of." Isn't the mapping of buses to settlement points contained in another posting? If yes, why should it be posted twice? |  | 10 | 0.3
Wagner | 3.10.3(3) | Requires the CRR model to include "data inputs used in the calculation of Dynamic Ratings." Since the auctions are month by month, wouldn't the ratings be static for peak and off peak by day? So are they asking for a table of daily peak and off peak ratings (assumptions) for the equipment with dynamic ratings? |  | 10 | 0.3
Doug Evans | 3.10.3(3)a | Is the current ERCOT map sufficient for a system oneline? |  | 10 | 0.3
Wagner | 3.10.4(3) | Require the installation of a "test and simulation facility that accommodates execution of the State Estimator and LMP calculator…" The RT operational system of the Texas Nodal is using ex-ante pricing, thus LMPs are a result of the dispatch algorithm and not the product of an LMP calculator which is "fed" with the actual operating data and then calculates LMPs. Thus it appears to indicate that ERCOT will need an LMP calculator in addition to the dispatch software. Is this the case? |  | 10 | 0.4
Lee Caylor /Curtis Crews | 3.10.7.1(2) | Please clarify requirements for co-owned transmission elements (quite possibly named differently at each partial owners control center) |  | 10 | 0.7
Doug Evans | 3.10.7.1.1(2) | Add an (h) for the line length as data that the TSP shall provide |  | 10 | 0.7
Doug Evans | 3.10.7.1.1(2)(g) | Add "rating for transformer or conductor that does not include ancillary equipment" as data that the TSP shall provide |  | 10 | 0.7
Jay Dondeti | 3.10.7.1.1(2)(e) 3.10.7.1.2 3.10.7.1.2 (1) 3.10.7.1.2 (3) 3.10.7.1.3 (1) | Please clarify the definition of an Electrical Bus. Lines are not covered in the definition of Electrical Bus. In item (3) of this section it is mentioned that a separate name can be given to each electrical bus that can be seperated by manual switch or breaker. In HUB definitions LPCCS station contains only one electrical bus. From the breaker configuration this station 345 kv circuit can be split into two electrical buses. It is not clear how the electrical buses are defined and how they are associated to Hubs. Don't we need the KV level and a primary node for each electrical bus to uniquely identify. And may be we need to represent all nodes that are part of the electrical bus. Transmissions lines attributes include from and to electrical buses, but not KV level. It seems the KV level is needed on the electrical buses. |  | 10 | 0.7
Doug Evans | 3.10.7.1.4(3) | Currently, neither Planning or Operations models the substation service load that is commonly served from the tertiary. Is it the intent that every station service will be modeled explicitly? Should there be a threshold? |  | 10 | 0.7
Lee Caylor /Curtis Crews | 3.10.7.1.4 (4) | Change in Tap position timing requirements violate 3.10 (6) which states "ERCOT shall use a Network Operations Model Change Request (NOMCR) process to control all information entering the Network Operations Model." in terms of timeframes associated with NOMCR process. Please clarify |  | 10 | 0.7
Lee Caylor /Curtis Crews | 3.10.7.1.4 (4) | " If mutual agreement cannot be reached, then ERCOT shall decide where to set the tap position to be implemented by the Generation Entity…" Please confirm ERCOT should staff to determine proper tap positions. |  | 10 | 0.7
Mark Patterson | 3.10.7.2 (1) | Due to existing issues some specific language concerning Private Networks should be included. The current language is not specific enough to cover the requirments of large generating units back behind private networks. |  | 10 | 0.7
Lee Caylor /Curtis Crews | 3.10.7.2 (1) | Clarify "consistency between TSP models and ERCOT models". Model data may be provided to TSPs but ERCOT can not coordinate consistency nor enforce it at a TSP level. |  | 10 | 0.7
Doug Evans | 3.10.7.4.1(2) | ERCOT seeks guidance on who/what will establish performance metrics. Assume it will be the TAC appointed task force? |  | 10 | 0.7
Lee Caylor /Curtis Crews | 3.10.7.4.2 (5) | This could become an overwhelming task - would suggest combining this section with performance metrics. Is the 5% or 5 MW too onerous? Consider higher threshold and tighten as market matures? Will there be too many alarms given? |  | 10 | 0.7
John Adams | 3.10.8(1) | Unclear on why ERCOT should use dynamic ratings on the Annual Planning Models, which are already for summer peak. Do you want ERCOT to derate dynamically rated lines because there is a change of higher temperatures then design? What temperature should be used for planning is a question? Will future summer peak models use the same temperatures for each year? How will the temperatures for future cases be predicted by weather or load zone, by bus, or one temperature for the whole state? Attempt to use same 10-year temperature averages as for CRRs? |  | 10 | 0.8 | 0
Doug Evans | 3.10.8(4) 3.10.8.5(a) | Why limit this to 12 elements per year? ERCOT believes this number came from the old pilot project- recommend deleting the limit of 12. |  | 10 | 0.8 | 0
John Adams | 3.10.8(4) | The sentence "ERCOT shall use the most limiting rating and report the circumstances to the Wholesale Electric Market Monitor" is very unclear. What does ERCOT report to the market monitor? Lines that are shared between TDSPs are often different due to different line rating methodologies and characteristics utilized by the companies. |  | 10 | 0.8 | 0
John Adams | 3.10.8.1 | The system described here is not quite the same as our current dynamic rating system. Was a redesign intended? Our current dynamic rating system accepts updates more often than once/hour for the next hour. It accepts changes at any time for right now. When the hour ahead study is run it uses the next hours temperature to calculate ratings. ERCOT Operations would advise against using the last provided dynamic ratings when telemetry is not operational. Currently ERCOT reverts to the nominal rating for loss of telemetry. Continuing to use an old dynamic rating is very high risk. Are there any time limits associated with the loss of data? |  | 10 | 0.8 | 1
Lee Caylor /Curtis Crews | 3.10.8.1(2) | "Dynamic ratings may be updated via telephone." For a rating change would email an immediate email, followed by Service Request for permanent change. If referring to telemetry updates, this is not a feasible solution. |  | 10 | 0.8 | 1
Lee Caylor /Curtis Crews | 3.10.8.2 (1) | Please clarify requirements for Interzonal and co-owned Dynamically rated lines. (basically add an "s" to d and e) |  | 10 | 0.8 | 2
John Adams | 3.10.8.2(2) | Requiring that a TSP update temperatures to ERCOT in event of loss of telemetry in the scada system is not practical. Currently ERCOT uses its own temperature monitoring system if the TDSP source fails. Is a change to this necessary? |  | 10 | 0.8 | 2
Lee Caylor /Curtis Crews | 3.10.8.3 | This section states that dynamic ratings are implemented automatically within 24 hours of receipt. Section 3.10.8.1(2) conflicts with this automatic update requirement when ratings are updated via telphone calls. Conflicts exist in 3.10 (3) regarding postings of all equipment ratings on the day prior to implementation. Additional conflicts exist in 3.10 (6) which states "ERCOT shall use a Network Operations Model Change Request (NOMCR) process to control all information entering the Network Operations Model." This requirement also seems to conflictingly imply that any Dynamic Rating changes would require a report to the PUCT and WEMM per 3.10.4 (4). |  | 10 | 0.8 | 3
Lee Caylor /Curtis Crews | 3.10.8.4(2) | No explicit requirements for planning how to estimate the temperature- in 3.11 Transmission Planning or 3.10.2. Please clarify responsibilities in Planning model (3.10.2). |  | 10 | 0.8 | 4
Lee Caylor /Curtis Crews | 3.10.8.5(c) | Temperature update "every 10 minutes" vs. others hourly (example 3.10.8.2(2)) |  | 10 | 0.8 | 5
Jay Dondeti | 3.10.9.2 | What does it mean by monitoring the performance of NSA, SCED, and LMP Calculator. What are the performance variables and standards for these variables? |  | 10 | 0.9 | 0
Jay Dondeti | 3.12.2 | What is interaction or depedency or connection between Long-Term Load Forecast and Long-Term Demand Forecasts of section 3.2.2 |  | 12 | 2
Wagner | 3.14.1(1) | Use RMR …"where market solutions do not exist" What does "market solution" mean in the context of Nodal? |  | 14 | 1 | 0
Wagner | 3.14.1.2(1) | Reference to title of 3.14.1.1 is inconsistent with title of that section. (An "s" on Operations is in the Title and not in the paragraph reference.) Should this be fixed? |  | 14 | 1 | 2
Wagner | 3.14.1.10(1) | Discusses Incentive Factor payments for RMR Units. States, "The Incentive Factor for RMR Agreements is not applied to capital expenditures as described in Section 3.14.1, Reliability Must Run." No area of the section prior to this reference discusses "capital expenditures." This term needs to be fleshed out or the reference should be changed to "any capital expenditures for maintenance items, and 3.14.1.11, Major Equipment Modifications." |  | 14 | 1 | 10
Steve Reedy | 3.15 & Section 2 | VOLTAGE SUPPORT: In most places the new protocols look similar to the old protocols in regards to Voltage Support. However, there are some problems. The main problem is that it is not defined as to where the URL is measured, and furthermore, it is defined improperly in the definition section. CURRENT ZONAL LANGUAGE: 6.5.7.1 Generation Resources Required to Provide VSS Installed Reactive Capability (1) Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power at rated capability (MW) to maintain a Voltage Profile established by ERCOT. This quantity of Reactive Power is the Unit Reactive Limit (URL). (2) Generation Resources required to provide VSS except as noted below in items (3) or (4), shall have and maintain a URL which has an over-excited (lagging) power factor capability of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the transmission grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the point of interconnection to the TDSP. ORIGINAL NODAL LANGUAGE: Unit Reactive Limit The maximum quantity of Reactive Power that a Generation Resource is capable of providing at a .95 power factor at its maximum Real Power capability. PROPOSED NEW NODAL LANGUAGE Unit Reactive Limit (Lagging) The amount of Reactive Power which, when produced while a Generation Resource is operating at maximum Real Power capability, produces a 0.95 power factor at the point of interconnection to the TDSP. (Leading) The amount of Reactive Power which, when absorbed while a Generation Resource is operating at maximum Real Power capability, produces a 0.95 power factor at the point of interconnection to the TDSP. |  | 15 | 0 | 0
Steve Reedy | 3.15(3) | ORIGINAL LANGUAGE 3.15 (3) Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power (MVars) at a .95 power factor at the Resource’s maximum rated real power capability (MWs) to maintain a Voltage Profile established by ERCOT. This quantity of Reactive Power is the Unit Reactive Limit (URL). PROPOSED LANGUAGE:3.15 (3) Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power (MVars) at a .95 power factor measured at the Resource’s maximum rated real power capability (MWs) and at the point of interconnection to the TDSP to maintain a Voltage Profile established by ERCOT. This quantity of Reactive Power is the Unit Reactive Limit (URL). |  | 15 | 0 | 3
Trip Doggett | 3.16(7) | We assume the 50% limit is 50% of the QSE's RRS allocation, not the total ERCOT RRS requirement described in 3.16(6)? If 50% of the total ERCOT requirement, what does ERCOT do if the sum of multiple QSEs self-arrangement exceeds the 3.16(6) ERCOT limit? |  | 16 | 0 | 7
Mark Patterson | 3.18 (4) | For Load Resources providing NSRS shouldn't the limit be less than or equal to (MPC-LPC) and not the LPC? |  | 18 | 0 | 4