| OGRR Number | 179 | OGRR Title | Under-Voltage Load Shedding Protection Systems |
| --- | --- | --- | --- |
| Operating Guide Section Requiring Revision | 7.2.5.3, Specific Application Considerations |
| Protocol Section Requiring Revision, if any. | None |
| Requested Resolution | Normal |
| Revision Description | Requirements for under-voltage Load shedding protection systems and minor modifications for references to supporting Sections of the Operating Guide (regarding protection system maintenance). |
| Reason for Revision | To satisfy ERCOT requirements relating to under-voltage Load shedding implementation by individual utilities. |
| Timeline |
| Date Posted | 1/05/06 |
| Please see the Master List on the ERCOT website for current timeline information. |

| Sponsor |
| --- |
| Name | Mehrdad Vatani, Chair, on behalf of the System Protection Working Group |
| E-mail Address | Mehrdad.vatani@austinenergy.com |
| Company | Austin Energy |
| Company Address |  |
| Phone Number | 512-505-7149 |
| Fax Number |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact | Benefit |
| --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | None | None | Operating Guides clearer and more accurate |
| MARKET SEGMENT |  |  |  |
| Consumer | None | None | Operating Guides clearer and more accurate |
| LSE: General, Including NOIE | None | None | Operating Guides clearer and more accurate |
| LSE: CR & REP | None | None | Operating Guides clearer and more accurate |
| QSE | None | None | Operating Guides clearer and more accurate |
| Resource | None | None | Operating Guides clearer and more accurate |
| TDSP | None | None | Operating Guides clearer and more accurate |

Proposed Operating Guide Language Revision

#### 7.2.5.3	Specific Application Considerations

Automatic Under-Frequency Load Shedding Protection Systems

Automatic under-frequency Load shedding systems are classified as protective relay systems.  The maintenance requirements, discussed in Section 7.2.4, apply to under-frequency Load shedding protection systems as well.

1.	Automatic under-frequency Load shedding systems are generally located on equipment operated below 60 kV; however, they have a direct effect on the operation of the system during major emergencies.

2.	The criteria for the operation of these protection systems are detailed in Operating Guide 2.9  - Requirements for Under-Frequency Relaying.

3.	Automatic under-frequency Load shedding protection systems need not be duplicated.

4.	Generator and turbine under-frequency protection systems shall be coordinated with Operating Guide 2.9 - Requirements for Under-Frequency Relaying.

5.	On pressurized water reactor steam supply units where under-frequency related protection systems are installed to detect loss of coolant flow condition, these protection systems shall be coordinated with the automatic under-frequency load shedding program.

6.	Automatic Load restoration for a UFLS operation is not currently utilized in ERCOT.

Automatic Under-Voltage Load Shedding Protection Systems

Automatic under-voltage Load shedding systems are classified as protective relay systems. The maintenance requirements, discussed in Section 7.2.4, apply to under-voltage Load shedding protection systems as well.

1.	The requirement for under-voltage relaying shall be determined by system studies performed / administered by ERCOT designated working groups or equipment owners. The system studies should indicate the following:

Amount of Load to be shed to restore voltage to minimum acceptable level or higher,

The minimum and maximum time delay allowed before automatically shedding Load,

The voltage level(s) at which to initiate automatic relay operation, and

The location(s) for effectively applying under-voltage Load shedding protection systems.

2.	Automatic under-voltage Load shedding protection systems need not be duplicated.

3.	Generator under-voltage protection systems and automatic under-voltage Load shedding protection systems shall be coordinated.  If the two systems cannot be coordinated, this should be reported to and reviewed by the ERCOT designated working groups or equipment owners performing the system study of item (1) above.

4.	Under-voltage protection systems shall be designed to coordinate with other protective devices and control schemes during momentary voltage dips, sustained faults, low voltages caused by stalled motors, motor starting, etc.

5.	Automatic Load restoration for a UVLS operation is not currently utilized in ERCOT.

6.	The scheme shall be designed to ensure reliable operation and to prevent false tripping.