- Dynamics Working Group

Procedural Manual

DRAFT

Revision 3

ROS Approved

TBD

# TABLE OF CONTENTS

Foreword	3

I.	Introduction	4

II.	Data Requirements	5

A.	Types of Dynamics Data Needed	5

B.	Dynamics Data Storage	5

C.	New Dynamics Data	5

III.	Dynamic Data Screening Procedures	8

IV.	Annual Data Filing and Distribution	10

V.	Annual Dynamics Data Update Schedule	11

VI.	Dynamic Disturbance Recording (DDR) Equipment	12

VII.	Event Simulation	12

VIII.	Procedural Manual Revision Guidelines	12

IX.	Flat Start Tutorial	13

A.	No Wind data inclusion into load-flow cases and dynamic data base	13

B.	Wind data inclusion into load-flow cases and dynamic data base	24

X.	Transient Voltage Stability Study Procedure	29

ERCOT TVS criteria	30

Sample System Transient Voltage Stability Analysis	30

XI.	Dynamics Working Group 2005 Roster	38

# Foreword

This Procedural Manual is intended for use by the stakeholder members of the Electric Reliability Council of Texas (ERCOT) for the purpose of creating and maintaining the dynamics database and dynamics simulation cases which are used to evaluate the dynamic performance of the ERCOT system.

The majority of ERCOT member utilities utilize Power Technologies Inc. (PTI) Power System Simulator (PSS/E) software.  Consequently, the various activities in the procedural manual incorporate PTI procedures and nomenclature in describing these activities. Wherever possible, a description of the PTI activity is given so users of software other than PTI may implement similar actions.

# Introduction

To adequately simulate the behavior of the ERCOT system it is necessary to develop and maintain dynamic simulation-ready base cases and associated dynamics data files using actual equipment data together with appropriate dynamic simulation software.  The ERCOT Steady State Working Group (SSWG) power flow cases provide transmission system representations which, along with the dynamics database, are used by the Dynamics Working Group (DWG) to create dynamic simulation cases ready to run under PTI’s PSS/E software.

Each ERCOT area, as defined in the base case, shall have a data owner who is responsible for submitting all the dynamic data required by DWG for that area.  Such a data owner should be identified in the DWG members list and updated as needed.  All dynamic data and updates are received by a DWG member as assigned by the DWG Chair.  Then dynamic simulation cases for the current year and a future year determined annually by the Working Group are created. This process is repeated annually.

# Data Requirements

## Types of Dynamics Data Needed

Generator dynamics data includes generator, governor, excitation system, power system stabilizer, and excitation limiters.  Other types of data needed for dynamics study unrelated to the generator include load shedding relay data, protective relay data, FACTS devices (e.g., DVARS, SVC, STATCOM, SMES), DC connections and load model data.

## Dynamics Data Storage

ERCOT shall be responsible for storing all of the dynamics data obtained from interconnected generators.  It shall maintain a repository of dynamics data in paper form, PSS/E datasheets and records formats with tuned parameters and will maintain the submitted revisions. All of the generator data received by ERCOT shall be forwarded to the DWG member of the TDSP to which the generator is connected.  ERCOT staff shall inform the ERCOT compliance team if any data is missing or has not been made available.

## New Dynamics Data

Whenever new generation capacity larger than 10 MW connects to the ERCOT system, the Generating Entity (GE) or Power Generation Company (PGC) connecting the generation is required to go through the formal “ERCOT Generation Interconnection Request or Change Procedure”.  An integral part of this process is the submission of dynamic data for each unit.  As stated in the ERCOT Generation Interconnection Request or Change Procedure dated 7/23/2004: “Therefore, the GE or PGC is required to submit specific information regarding the electrical characteristics of their proposed facilities with their request.  Failure to supply the required data will result in delay of the study, and may adversely influence reliability or result in damage to generation equipment… The most current facility data or expected performance data should be submitted to ERCOT with the initial study request.  Data submitted for stability models shall be compatible with ERCOT standard models.  If there is no compatible model(s), the GE or PGC is required to work with a consultant and/or software vendor to develop and supply accurate/appropriate models along with associated data.”  The GE or PGC must provide all paper and/or electronic documents containing manufacturer’s data describing the electrical characteristics of the generator.  The data also must be provided in the form of PSS/E model data sheets and dynamics model records with tuned parameters. Classical model data is not acceptable.

In summary, GE’s or PGC’s are responsible for tuning generator model parameters and providing PSS/E data sheets and model records to ERCOT. The final responsibility for the submission and the accuracy of the data lies on the GE’s or PGC’s. However, ERCOT and the DWG will provide voluntary assistance if requested by GE’s or PGC’s to complete parameter tuning and preparing PSS/E model records. ERCOT will serve as the single point of contact to facilitate these activities. The DWG member of the TDSP to which the generator is connected is responsible for incorporating the dynamics data received from the GE or PGC into the ERCOT Dynamics database during annual updates.

### Revising Dynamics Data

The DWG is responsible for reviewing the tuned model parameters on an annual basis, and reporting any missing data or unresolved issues relating to data submission requirements to the ROS. If there are any problems with the data, the DWG will work through ERCOT with the GE’s or PGC’s to resolve the problems. However, the final responsibility for the submission and the accuracy of the data lies on the GE’s and PGC’s. All of the data and the revisions requested by ERCOT from the GE’s or PGC’s shall be resolved by GE’s or PGC’s within 30 days.  Also, any change in generator modeling parameters determined either through field testing or after changing relevant equipment or equipment settings should be reported to ERCOT by GE’s or PGC’s within 30 days.

Data that is currently valid does not have to be resubmitted to ERCOT by GE’s or PGC’.

For revisions to the existing dynamics data, the DWG utilizes the previous year’s dynamics data. Each DWG member sends revisions in their DYRE files back to the designated DWG member in CSV format.

The DWG will generally not make changes to existing data unless modification of generating units or field testing have occurred.  Examples of modifications include replacement of an old excitation system with a new, static excitation system or boiler/turbine upgrades.  The dynamics data has been tuned throughout the years to ensure proper operation of the models and original manufacturer’s data may have been modified during this process; therefore, the parameters in the ERCOT dynamics database should not be changed to match manufacturer’s data, unless it is absolutely certain that the data is correct.  Obsolete data should be deleted. However, data for mothballed units shall be retained.

Other revisions of data that should be submitted to the designated DWG member include updates to the load model (CONL), Zsource corrections, generation netting, or any other modifications to the network necessary for dynamic studies.

### Load Acting As a Resource (LaaR, high-set relays for frequency set points above 59.3 Hz)

Upon installation of an underfrequency interruptible load shedding relay for LaaR, ERCOT shall provide the load and relay data to the associated DWG member.  The DWG member of that TDSP will provide the corresponding PSS/E relay model to ERCOT during the annual data update or as needed for ERCOT study.  The models should contain the necessary information to properly represent the high set relay actions in a dynamic study.

### Underfrequency Firm Load Shedding Relay Data (UFLS)

ERCOT shall collect the underfrequency firm load shedding relay data on an annual basis.  The DWG shall prepare the PSS/E relay model records when needed for a UFLS study.  Each DWG member is responsible for preparing the UFLS PSS/E relay model records for the loads within their TDSP.  The models should contain the necessary information to properly represent the UFLS relay actions in a dynamic study.

### Undervoltage Load Shedding Relay Data

After installation of any undervoltage load shedding (UVLS) relays, the DWG member of the TDSP installing the relays will submit the corresponding PSS/E relay model to the designated DWG member during the annual data update or as needed for DWG studies.  The models should contain the necessary information to properly represent the undervoltage relay actions in a dynamic study.

### Protective Relay Data

The operation of protection, control, and special protection systems can affect the dynamic performance of the ERCOT system during and following contingencies. Planning, documenting, maintaining, or other activities associated with these systems is outside the scope of the DWG. However, because they can affect dynamic performance, the DWG should, on an as needed basis, identify and document protection, control, and special protection systems, which affect multiple transmission providers. Identification activities will normally require the assistance of individuals or groups outside the DWG. The specific information to be considered for inclusion will depend on the type, purpose, and scope of study.

Protection, control, and special protection systems included in the DWG database should be in the form of a standard PSS/E model or models. A descriptive model, such as a time-based sequence of events, is also acceptable. Protection, control, and special protection systems adequately modeled for dynamic purposes by other working groups only need to be referenced in the DWG study reports.

The PSS/E software contains several models, such as OSSCAN and RELAY1, which may be used to indicate situations where actual protection, control, and special protection systems should be included in a simulation (After PSS/E Rev. 28, such models are replaced with “simulation calculation options”. See Program Operations Manual Vol. 1 Section 5.31.).

The DWG member, as part of the annual database update, shall review and update as necessary protection, control, and special protection systems already in the DWG database. This review should include evaluating the existing data for applicability and accuracy. Obsolete data should be deleted.  These updates may also be required as needed to perform ERCOT dynamic studies.

### Other Types of Dynamics Data

After installation of any other dynamic element located on the transmission system such as an SVC, STATCOM, SMES, and DC ties, the DWG member of the TDSP owning the equipment will provide the corresponding PSS/E model to the designated DWG member during the annual database update or as needed for DWG studies.

### Missing Dynamics Data

Each DWG member shall provide a list of dynamics devices without the appropriate dynamic data to the designated DWG member.  The DWG should identify and document missing dynamics data, models, protection data, and special protection systems, for which data is not available.  The DWG Chair will inform the ERCOT compliance team if any data is missing or has not been made available. Until valid data becomes available, the DWG member to whose system the generator is connected shall recommend an interim solution to the modeling problem.

# Dynamic Data Screening Procedures

Each DWG member must perform dynamics data screening before submitting data for inclusion in updated dynamics base  cases.  Included in the data screening check should be, as a minimum, the items listed and described below.

The dynamics data provided by GE’s and PGC’s should reflect accurate modeling information as described in Section II.C. Each DWG member should verify that the data is complete and reasonable.

- DWG data should be compatible with the SSWG power flow base cases.  Currently, the SSWG cases are developed using the PSS/E software package.

- Units and plants should be represented as follows: (These principles do not necessarily apply to wind generation modeling which will be covered in a future section)

1.	Units should not be lumped together.

2.	A unit’s step-up transformer should be modeled explicitly. This should already be the case in the SSWG base cases.

3.	A unit’s total Qmax should not contain external power factor correction capacitors netted into it.  Such capacitors should be modeled explicitly in the Switched Shunt data block of the base cases.

4.	New generation less than 10 MVA may be netted out. Older plants with total generation less than 50 MVA may be netted out.

- Each unit should have consistent unit identifiers from year to year.  PSS/E format allows a two-character alphanumeric field.  This must be coordinated through the SSWG.

- Dynamics data must be provided in machine MVA base.

- Unit data must be supplied using its own machine base and machine kV base, and must be represented correctly

- Zsource data provided in the SSWG base cases must match the dynamics data.  Zsource must be the unsaturated subtransient reactance of the machine (X”di) for GENROU, GENSAL, GENDCO, and FRECHG models and must be the transient reactance X’d for the GENTRA models.

- If data in 1 or 2 is incorrect, the responsible DWG member will submit data to correct the discrepancies.

- Units that are not dispatched should have dynamics models and data in the dynamics database for completeness of data so that alternative dispatch scenarios may be studied.

- Unit data checks

- Realistic values (Actual values determined from unit testing should be used whenever possible) should be used for Pmin, Pmax, Qmin, and Qmax.  The Pmax value in the dynamics data should match the Pmax value used in the load flow data.

With very rare exceptions, small changes in a machine’s Pmax value are not significant for study purposes.  DWG will take the following approach during flat start activities:

- Create a program to change the current year load flow case Pmax values to last years values unless the Pmax value has changed by more than 5 % (10 % for 2006 flat start activities).

- Where the Pmax has changed by more than 5 %, examine the new value and ascertain the reasonableness of the new Pmax.

- If the Pmax change is reasonable, change the load flow case and the dynamics database to the new value.

- Follow this procedure for 2006 and future year summer case flat start activities.

Use of default values is not acceptable for both power flow and dynamics data.  This must be coordinated with the SSWG.

- Screening checks shall be performed on the power flow model used in association with the dynamics data.  The following area examples of screening checks to be performed:

- Pgen + jQgen <= 115% of MVA base

- Qmax >= Qmin

- Zsource not equal to 1.0 pu

- Screening checks shall be performed on the dynamics data.  The following are examples of screening checks to be performed:

- Inertia constant should include both turbine and generator

- Generator reactance data is unsaturated

- Refer to the PSS/E Program Application Guide, Volume 2, Chapter 21 for use of activities DOCU, ESTR, ERUN, GSTR, and GRUN in data screening

- Station service/auxiliary load representation at the generation bus is at the discretion of the DWG member.

- User-defined models

User-written models should be compatible with PSS/E.

- DWG members must perform initialization of data with no errors and demonstrate that simulation output channels do not deviate from an acceptable range for a ten-second run with no disturbance. See Flat Start Procedure section.

# Annual Data Filing and Distribution

## Dynamics Data Base

Once the flat start for the required load flow cases has been completed, the dynamics data is distributed to each of the DWG members electronically in PTI format.  This dynamic data distribution must be within the schedule stated in the DWG Procedures.

## Stability Book

The stability book is used to document dynamics data changes and/or corrections required during the flat start process. Recommendations to revise load flow data are also included in the book. DWG Members are required to communicate these recommendations to their respective SSWG member to eliminate recurring problems.

To verify the successful completion of the flat start process, this book should also contain plots of the flat start results. The plots should include, at a minimum, the six (6) worst units (based on angle deviation).

The dynamics data is also included in the stability book. This data is in the DOCU ALL PTI format.

Also included in the stability book is the load shedding relay data submitted by each of the appropriate Dynamics Working Group members.

# Annual Dynamics Data Update Schedule

## Initiating Annual Dynamics Data Update

The DWG Chair, following the DWG annual schedule, will initiate the dynamic data collection by assigning a DWG member to perform the flat start process and to whom all DWG members will send their updated dynamics data in electronic format.  An electronic copy of all dynamics data and final data files after the flat start process is completed will be sent to ERCOT System Planning for archiving.

## Model and data review by DWG members

DWG members are the recipients of dynamics models and data. The information received should be reviewed for completeness and applicability as described in sections III and IV of this procedure. The data should be appropriate for the model, and the model should be appropriate for the equipment.  The ‘ERCOT Modeling Guide for Dynamic Stability’ provides additional information about modeling. If there are questions or problems, the DWG member should discuss and resolve them with the power source owner.

## Flat Start

The designated DWG member will add all of the updates to the ERCOT dynamics database and perform a flat start as described in section VII of this procedure. The designated DWG member  will contact the appropriate DWG member to resolve any problems with the data encountered during the flat start process. The DWG will annually determine a schedule for completion of all flat start activities.

# Dynamic Disturbance Recording (DDR) Equipment Annual Review

ERCOT and the Dynamics Working Group shall prepare a list and perform an annual review of facilities that operate above 100 kV, are part of a dynamic stability (not transient stability) interface, and require the installation of a DDR.  ERCOT and the Dynamics Working Group shall forward any revised DDR facility list to the Reliability and Operating Subcommittee (ROS) for its review and comment.

DDRs shall be removed or taken out of service by the same process.

For additional information on DDR, see the DWG proposed Operating Guide change.

# Event Simulation

From time to time DWG will simulate an actual disturbance event for the purpose of assessing the fidelity of the ERCOT dynamics models and data with actual system performance during the event.  DWG will perform these event simulations when requested by ROS.  In addition, DWG will annually consider recent significant events to determine their suitability for event simulation.  DWG will consider their work load and the type of information likely to be obtained in making a decision as to whether to simulate an event.

# Procedural Manual Revision Guidelines

The DWG is responsible for maintaining and updating this Procedural Manual. Revisions, additions and/or deletions to this Procedural Manual may be undertaken at such times that the DWG feels it is necessary due to changes in PTI dynamic simulation software or to meet new and/or revised requirements of NERC, ERCOT or any other organization having oversight or regulatory authority.

At least annually, the DWG Chair shall notify the DWG requesting each member to make a thorough review of the current Procedural Manual for any needed revisions. The notification will request that proposed revisions be submitted to the DWG Chair (or his designate) for consolidation and distribution to all DWG members for comment and/or additional revision. Depending on the magnitude and nature of the revisions being considered, this review process may require more than one cycle before approval is considered. The DWG Chair should give consideration to being able to complete the review and revision process in time to avoid any delays in collecting dynamic data or completing other DWG work.

The DWG Chair may seek approval of any revision, addition or deletion to the Procedural Manual by email vote, regular meeting or called special meeting as deemed necessary or requested by DWG membership.

# Flat Start Tutorial

A member designated by the DWG Chair will perform a flat start on the complete ERCOT database. The product of a successful flat start will be a simulation-ready base case (the unconverted base case) with its associated dynamic data files, user models and stability data change document and idv files

At present, the DWG performs flat start for the summer on-peak base case of the current year data set A and a future summer on-peak base case of the current year data set B as prepared and published by the ERCOT SSWG (i.e.: in 2004, the DWG performed flat start using the 2004 summer on-peak and the 2007 summer on-peak cases.)

What follows is an approach that can be used to perform flat start:

## Flat start with no dynamics models for Wind Plants

Directory Structure

All final files will be stored at the working folder level, while intermediate files used during the flat start process will be stored in separate subfolders within the working directory folder.  File names and folder location are reflected in the IDV files.  As an example, Fig.1 shows the tree directory for the working directory “2004CSC”.

Fig. 1 Working Folder Directories

As shown in Fig. 3, the flat start process requires the following iterative steps to produce a successful dynamic flat response to a no-disturbance simulation.  Any error along the steps or large departures from recommended practices will require user intervention and a re-start of the process.

Step 1: Update of data files

What to do: update the individual files using a suitable tool.

Output: updated data files

Base case update (*.sav)

The starting base case is derived from the latest Steady State Working Group base case as posted in the ERCOT website and could contain already implemented updates, zone modifications, deletion of type 4 buses, generation control adjustments, etc.  This initial base case is renamed “ercot.sav” and stored in the Case folder.

Typical additional updates to the base case include:

- changes to the network such as PGEN, PMAX, VSCHED,  Use CNTB to identify any  bus voltage control conflicts

- zsource value matching between the base case and the DYR file

- gnet of generators lacking dynamic models

- conl load model conversion

- conversion of generators

Each of the updates/corrections will be implemented via an IDV file.

Dynamic files update (*.dyr)

Each TDSP’s dynamic model data are compiled into DYR files and aggregated into a single file, “ercot.dyr” saved in the DYR folder.  User model calls will be also included in this final file.  Whenever a model data is flagged for errors during the flat start process, the original DYR file will be updated/corrected and a new “ercot.dyr” prepared.

User Models update (*.for, *.flx, *.obj, *.lib)

Most user models are ready for use, free of errors.  Only in rare situations, the model will need correction (such as wind farm models), requiring access to the model code in Fortran or Flex.  The updated model will be compiled into a Fortran Object (*.obj) and then grouped into a Fortran library (*.lib) or be used directly in the link process (Step 4)

Step 2:  Make a Converted Case

What to do: run PSS/e Dynamic module and then run MakeCnv.idv

Output: ercot.cnv, a converted case saved at the working folder level.

All the base case changes are implemented within a single master IDV file (MakeCnv.idv) which calls the corresponding IDVs files, iplan and PSS/e activities to produce a converted case “ercot.cnv” saved at the working folder level.  While it is recommended that the converted case converge within one (1) iteration using the TYSL solution method, two (2) is the practical number of iteration usually achieved. (Check the “progress screen”).

Below is the contents of MakeCnv.idv (as used in the 2004 flat start process)

MENU,OFF      /* MakeCnv.idv: read ercot.sv and convert it to ercot.cnv

LOFL

CASE

Case\ercot.sav

@input, "IDVs\Adj_Dispatch_2004.idv"

@input, "IDVs\cnp_changes 2004.idv" (CenterPoint Changes)

@input, "IDVs\Oncor_changes.idv"

@input, "IDVs\Aep_changes.idv"

@input, "IDVs\M_zsource_all07.idv"

@input, "IDVs\M_GNET07.idv"

@input, "IDVs\Ercot_ConL.idv"

Exec "iplan\LoadFLow.irf" "1"       <- run flat load flow

Exec "iplan\LoadFLow.irf"             <- run load flow

CONG

ORDR

FACT

TYSL

TYSL

SAVE

ERCOT.cnv

RTRN,FACT

@END

Step 3:  Make a Snap file

What to do: run MakeSnap.idv

Output:

ercot_angle.snp, a SNAP file with the generator ANGLE  set as a channel for all generators in the base case.

ercot_nochan.snp, a SNAP file with no channels, for the user to customize it.

conec.flx, conet.flx and compile.bat files, used during compilation

The data in the final “ercot.dyr” together with information on variables to be monitored during the simulation (channels) are processed to generate a SNAP file by running “MakeSnap.idv”.  Data files (conec.flx, conet.flx, compile.bat) with information about the user model calls are also prepared ready for the compiling process (Step 4).

If there are User Models, quit PSS/e and go to step 4, otherwise continue to Step 5.

Below is the contents of MakeSnap.idv (as used in the 2004 flat start process)

MENU,OFF      /* Makes a SNAP file

DYRE

DYR\ss07sum1_CSC_DWG.dyr

conec.flx

conet.flx

,,,

compile.bat

SNAP

ERCOT_nochan.snp

, , , , ,

BAT_CHSB 0 1     -1     -1     -1 1  1 0

SNAP

ERCOT_angle.snp

, , , , ,

ECHO

@END

Step 4:  Fortran compiling process

(Skip this step if there is no User Models in this flat start process)

What to do: Quit PSS/e, open a DOS window pointing to the working directory, set the correct paths for the Fortran compiler (run DFVARS.bat, also run SetPSSE29_patch.bat if PSSE path was incorrect) as needed and then run

C:\...\compile

C:\...\cload4

Or

C:\...\compile usermodel.flx  (if usermodel was used)

C:\...\cload4 usermodel

…

Output:  DSUSR.dll, a user model library callable by PSS/e.  Other files (conec.obj, conet.obj, dsusr.lib, dsusr.exp, dsusr.map) are created but not needed for the final run.

In step 5, during starting of PSS/e dynamics, DSUSR.dll will be loaded and used for the simulations.

Fig. 2  Screen Example of the Fortran compiling process

Step 5:  Running the Flat Start Simulation

What to do: re-start PSS/e, verify that the DSUSR.dll file in the working directory is loaded by looking into the PSS/e DOS window and then run the “RunFlat.idv”

Output:

RunFlat.err, file containing run messages.  Check for the “STRT” and the “INITIAL CONDITIONS SUSPECT” sections to detect errors.

RunFlat.out, the output data file ready for plotting

The flat start simulation runs for 10 seconds, using an integration step of ¼ cycle (0.004167) and other miscellaneous settings.

Below is the contents of RunFlat.idv (as used in the 2004 flat start process)

MENU,OFF      /* RunFlat.idv - flat start, run it after MakeSnap.idv

altr

6

Y

99,0.4,,0.4,

Y

,,0.004167,,,

N

N

0

0

BAT_SET_NETFRQ 1

BAT_SET_OSSCAN 1 0

BAT_SET_GENANG 1 180.00

BAT_SET_GENPWR 1   1.10

BAT_SET_VLTSCN 1   1.50  0.50

BAT_SET_RELSCN 0

PDEV

2 0 1

RunFlat.err

ODEV

2 1 1

RunFlat.err

STRT

RunFlat.out

0

RUN

10,99,15,0

Step 6:  Plotting the Flat Start simulation results

What to do: Start the PSS/e plotting tool, Pssplt.exe, which is pointing to the working directory and then execute “PlotFlat.idv”

Output:  in the report screen, list of 12 channels with “Worst Channel Deviation”

The user will complete the Plotting process by selecting 6 channels and plotting them.  The expected results to the no-disturbance simulation are six nearly straight “flat” lines.  Check the scale of the plots for y-axis scale too big. Acceptable range for the worst channel deviation is less than 0.001

CHANEL IDENTIFIER                        INITIAL VALUE    DEVIATION         TIME (SECONDS)

223  ANGL 12322 [ENTRAC1116.000] [1 ]     55.44         0.1549E-02       8.8049

366  ANGL 60000 [DSKY2 PP34.500] [1 ]     26.33         0.3777E-03      10.0007

Below is the contents of PlotFlat.idv (as used in the 2004 flat start process)

MENU,OFF      /* PlotFlat.idv: ID worst angle deviations

CHNF

RunFlat.out

RANG

1

SCAN

5

4

1 409

12

ECHO

@END

Makes the COMPILE.bat file, makes the SNAP file Ercot_angle.snp

COMPILE and CLOAD4 the user defined models into dsusr.dll

10 seconds run with 1/4

cycle integration step, data output to RunFlat.out

The maximum deviation channels are listed in the REPORT window.

The user completes the PLOT process by selecting the SIX worst deviation channels and plotting them

Flat start?

Done















Converts the modified base case and save it as Ercot.cnv

Fig. 3  Flat Run Process Cycle

run PSS/e Dynamics:
run MakeCnv.idv

Update
base case

*.sav

Update
dynamic file

*.dyr

Update
user model

UserM.for

run MakeSnap.idv
close  PSS/e

Switch to FORTRAN:

>COMPILE UserM

>CLOAD4 UserM

run PSS/e Dynamics:

run RunFlat.idv

run PSS/e Plotter:

run PlotFlat.idv

NO

YESNO

## PSS/e Dynamic Simulation Activities used to perform the flat start.

For more information refer to the PTI Program Application Guide Volume 2, Chapter 12.

Activities to make a converted case:

Activity LOFL

This activity is used to retrieve the load flow case. Select the ERCOT load flow case to be studied from the working directory

Activity RDCH – to make network changes

With this activity, network updates will be applied to the base case.

Also used to make zsource changes such the zsource value in the base case will match the value provided in the dynamic data (usually performed by executing a ZSORCE idv file.)

Activity GEOL ALL

This activity will list machine terminal conditions. Check for MBASE of 0 and correct. GEOL checks machine reactive loading against an assumed capability curve.   This calculation uses MBASE. Units operating outside of their reactive limit will show up “overloaded” and the reactive output should be reviewed and corrected if necessary. This activity must be used for screening the data. .

Activity FNSL OPT

This activity is used to solve the selected load flow case using the Full Newton-Raphson solution method. Modify load flow parameters if needed.

Activity GNET

(usually performed by executing a GNET idv file)

This activity converts a generator bus to a load bus for lack of dynamic models.

Activity CONL

(usually performed by executing a CONL idv file)

This activity converts constant MVA load to desired constant power, current, and admittance characteristics.

The three choices are:

1. Constant power – power remains constant, P= k

2. Constant current – power varies linearly with V, P= VI*

3. Constant admittance – power varies quadratically with V, P=V2*Y

Activity CONG ALL

This activity converts all on-line generators (fixed power and voltage source) to a NORTON current source equivalent that is used by the DYNAMICS program.

Activity ORDR

Produces an optimal ordering of the internal working matrices.

Activity FACT

Factorizes admittance matrix for activity TYSL

Activity TYSL

This activity is a triangularized Y matrix network solution used in dynamics studies. Cannot handle fixed power and voltage LOADFLOW generation representation. It produces very small mismatches (If TYSL takes more than two or three iterations to reach tolerance, review the original LOADFLOW until a good solution is obtained) so that initial conditions are good for dynamics.

Activity SAVE

This activity saves a load flow case.

Activity RTRN

Returns to DYNAMICS program

Activities to make a SNAP file

Activity DYRE

This activity reads in the dynamics data file created by ERCOT.

Note and document any error messages. You will be asked for the ”CONEC’’, ‘’CONET”, and “COMPILE” file name.

Activity CHSB

This activity is similar to the activity CHAN except that it allows the user to select a subsystem for monitoring simulation variables.

Activity CHAN

This activity selects the output channels to be stored during the dynamic simulation. Typically, ANGLE, PELECTRIC and ETERMINAL are selected. The bus number and machine number for each unit must be given for each output channel picked.

Activity SNAP

This activity stores the data associated with the modeling of dynamic equipment.  Execute SNAP and save the dynamics data to a snap file.

Activity STOP

Activities to Fortran compiling:

If DYRE places no model calls in CONEC or CONET, you will get the following message:

“NO MODEL CALLS IN CONNECTION SUBROUTINES – DYNAMICS SKELETON MAY BE USED”.

Skip the COMPILE and CLOAD4 steps.

If DYRE placed any model calls in CONEC or CONET, you will be instructed to “COMPILE AND CLOAD4 BEFORE RUNNING SIMULATIONS” See following paragraphs for details.

From DOS, open the WORKING directory. To perform the next two steps, the computer system must include a  FORTRAN compiler with all patches recommended by PTI.

From DOS and the working  directory:

Execute COMPILE

Execute CLOAD4

If user-defined models are present, they should be included on the command lines, for them to be compiled and linked as well.

Execute COMPILE MyUserModel

Execute CLOAD4   MyUserModel

This compile command links the user model, CONEC and CONET to PSS/E by creating a file called "DSUSR.DLL", a dynamic link library used by PSSDS4.

Activities to run a simulation:

PSS/e Dynamics first looks for the file "DSUSR.DLL" that is located in the

working directory, needed when user model are included.  If the dll file is not there, it will use the default copy located in PSSLIB, which does not contain any user models.

Activity RSTR

Read in the snapshot file saved during setup.

Activity LOFL

Activity CASE

Read in the converted  case saved during setup.

Activity ORDR

Activity FACT

Activity TYSL

Activity RTRN

Activity ALTR

This activity changes the solution parameters (6) time step (DELT) to 0.004167 Seconds (¼ cycle). Note that some induction machines may have very small time constants requiring time steps of 0.000104 seconds (1/16 cycle).

Activity STRT

This activity sets initial conditions and performs numerous data checks.

The number of errors may be too large so it is better to create an error file to save errors to. To do this:

Activity OPEN  - Give file name to save errors

Activity PDEV

You must check all initial conditions reported by STRT carefully. The initial load flow should converge in one iteration.  Note that a state is a variable with a constant initial value. A DSTATE is a time derivative of the sate variable. Since there are no disturbances, DSTATE should be zero.  The listed DSTATE values should be within 3% to 5% of the corresponding state value.

Also, upon completion, STRT instructs the user to enter the simulation output filename to be used by activity RUN in the dynamic simulation.  The user will also be asked to enter a snapshot filename to preserve the system initial conditions. No snapshot filename must be specified at this time.

Activity RUN

This activity does the numerical integration of the differential equations (the simulation). You must enter a value for TPAUSE and NPLT. TPAUSE is the duration of the simulation. To test the simulation setup, run the simulation for 10 seconds. NPLT is the interval in # of time steps to write the simulation output to the channel file for plotting (NLPT should be an odd number).

TPAUSE 	= 10

NPRT      	= 3

NPLT 		= 1

CRTPLT	= 3

Activity STOP

When the simulation is over, this activity terminates execution of PSSDS4.

Activities to plot the simulation run results

Run PSSPLT,  the PSS/E plotting program.

Activity CHNF

Enter name of simulation output channel file.

Activity RANG

This activity scales the output channels. Choose option which generates common scale (X).

Activity IDNT

This activity identifies the output channels. You must give it a range.  No identifier mask needs to be given.

Activity SCAN

Choose option for maximum angle spread Option (3)

Activity SLCT

This activity selects the output channels to be plotted once identified. The output channels are automatically scaled by the RANG activity but you should choose a scale that will be large enough for consistency and comparison purposes. Six channels may be plotted at a time.

Activity PLOT

This activity plots the output channels chosen. A title for the PLOT can be given.

Activity STOP

You must get out of PSSPLT before any plots will be made. Once you are out, you are asked for the number of copies wanted and the name of the plotting device.

## Flat start with dynamics models for Wind Plants

The Wind farms models for dynamics simulations may include addition of collector networks to the base case describing the wind farm with its equivalent generators, addition of dynamics model calls to the dynamic data and updating the corresponding wind machine user models if needed.

DWG uses PTI developed iplan programs that will update the base case and the dynamic file.  The iplan program to use will match the type of machine in the TDSP’s wind farm.  DWG modified the source of some iplan programs to facilitate the process, producing corresponding DWG version of the compiled iplan (*.irf).  Associated data files are prepared per wind farm as needed by the iplan program.

Directory Structure

All final files will be stored at the working folder level, while intermediate files used during the flat process will be stored in separate subfolders within the working directory folder.  File names and folder location are reflected in the IDV files.  Table XX shows a recommended tree directory for the “07FlatWind” working directory.

There is a folder per each TDSP containing subfolders per each wind farm.  All data require to run the iplan programs are stored in the individual wind farm folder.

Iplan runs

For an individual wind farm, a single IDV file will execute all commands needed to modify the base case and create individual *.dyr files.  For a TDSP, a global IDV file will process all wind farms IDVs at once.  The modified base case is saved as ErcotWind.sav (stored in the CASE folder) and the individuals *.dyr files created per wind farm are aggregated into a single TDSP.dyr file (stored in the DYR folder.)

Fig. 4 shows the steps needed to incorporate the wind farm dynamic model into the simulation.  Notice that once the iplans have been run and the ErcotWind.lib file has been created (as described in the next section), the steps to follow are very similar to those in a common flat start process.

Aggregation of dynamics data

This process will produce a single *.dyr file for all the wind farms connected to each TDSP and together with the original ercot.dyr file (dynamics data not including wind farm data) these files are aggregated into a file named “ercotwind.dyr”  Such process is done by running the “MakeErcotWinddyr.idv” located in the DYR folder.

Fig. 4  Flat Start incorporating Wind farm Dynamics Models

Table 1 - Directory and files to include Wind Machines models

| 07FlatWind directory tree | Files in 07FlatWind |
| --- | --- |
| TDSP’s Wind Farms Directory Tree | Wind Farms Directory Tree (TWPP) |
| TDSP’s Global IDV file for all Wind Farms | Wind Farm IDV file (TWPP) |
| Text, ALL LCRA Wind Farms @input DelawareMWF_main.idv SAVE '..\Case\BC0+DelawareMWF' @input TWPP_main.idv SAVE '..\Case\BC1+TWPP' SAVE '..\Case\ERCOTwind.sav' Exec "..\Ipl\append.irf" "*.dyr" "..\Dyr\lcraWind.dyr" @end Text, End ALL LCRA Wind Farms. | TEXT, TEXAS WIND POWER PARTNERS @input TWPP\TWPP_KT_Collector_Bus_Details.IDV Exec "..\ipl\LoadFLow.irf" "1" EXEC ..\WINDMACHINES\STATIC\STATIC3_DWGR2.IRF @input TWPP\TWPP_KT_Dialog.idv Exec ..\Ipl\LoadFlow.irf @end TEXT, END OF TEXAS WIND POWER PARTNERS |

Making the Ercot Wind Library

Fortran Source Code Update

Whenever a Fortran source code (*.for) of a wind machine dynamic model needs to be corrected or updated, such source code will be compiled to create an OBJECT file (*.obj)  From an open DOS window within such model folder, run the corresponding XXX_compile.bat file to compile all *.for files into their corresponding *.obj files.

Machine Library

For each machine there is a collection of *.obj files which will be aggregated into a single library file.  Updates to the model by PTI or the developer of the wind machine may be distributed only in *.obj format or *.lib format.  From an open DOS window within such model folder, run the corresponding XXX_make_lib.bat file to store all *.obj files into a single XXX.lib file.

Table 2 - Directory and files to process Wind Machines model objects

| Wind Machines Directory Tree | Wind Machine files (GE1500) |
| --- | --- |
| Objects Directory | CreateERCOTwindLib.bat |
|  | @REM LIB /OUT:..\ERCOTWIND.lib GE1500/OBJECTS/GE1500.lib V47/OBJECTS/V47.lib V80/OBJECTS/V80.lib MICONnm72/OBJECTS/NM72.lib SHARED/OBJECTS/SHARED.lib STATIC/OBJECTS/STATIC.lib @REM Done creating the ERCOT WIND object library |

ErcotWind.lib (aggregation of all machine’s *.lib file) is built by running the MakeERCOTWindLib.bat from an open DOS window at the Wind Machines folder

Flat Start Run with Wind Machine Models included

The user will proceed with the flat start as described in Fig. 4:

- run MakeCnv.idv

- run MakeSnap.idv

- Fortran-compile the wind farm user models

- run RunFlat.idv

- run PlotFlat.idv

If any error is reported along the steps or large deviation of output values are found after the runs, the process shall be repeated after correcting/updating data where appropriate.

# Transient Voltage Stability Study Procedure

In 2003, the DWG developed the document “ERCOT Transient Voltage Security Criteria Development (Part I)” to address a request from the ROS on the subject of transient voltage criteria.  Included in that document was a detailed procedure for conducting a transient voltage study.

# Dynamics Working Group 2005 Roster

At least one entry per ERCOT area as defined in the base cases:

Austin Energy				Reza Ebrahimian

AEP					Vance Beauregard

CPS Energy				Michael Spence

GGTMPA                                             Danh Huynh

CenterPoint  Energy                            Wesley Woitt	, Vice Chair

Lower Colorado River Authority	Tom Bao

Public Utilities of Brownsville		James McCann

South Texas Electric Cooperative	John Moore

TXU Electric Delivery		           Roy Boyer, Chair

TNMP					Anthony Hudson

ERCOT System Planning		Jose Conto

ERCOT System Planning		John Schmall

ERCOT Operations                             Yan Ou

PTI has authorized use of PTI information to be included in this Procedural Manual.