## ERCOT Operations Report

## ROS & OWG

## December 2005

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 12/3/05 18:13 | 59.897 | 33631 | 1000 | -388 | Five QSE with total SCE = -372 |
| 12/5/05 6:10 | 59.899 | 35004 | 910 | -23 | 3800 (1030) |
| 12/13/05 5:05 | 59.885 | 29525 | 300 | -339 | 1450 (280) |
| 12/13/05 18:18 | 60.101 | 34354 | -1179 | -444 | High frequency aligns with drop off of evening peak. |
| 12/19/05 2:06 | 60.146 | 28086 | -518 | -201 | Balanced 1180 Up over interval. |
| 12/30/05 6:03 | 60.109 | 25338 | -1025 | 444 | 2000 (430) |

| Disturbance Data |  |  |
| --- | --- | --- |
| 12/9/05 12:16 | 60.102 | 455 MW obligation lost |
| 12/9/05 17:11 | 59.863 | 565 MW resource lost |
| 12/13/05 13:33 | 59.869 | 2 units, 445 MW |
| 12/15/05 7:16 | 59.887 | 700 MW run back and trip at a station. |
| 12/31/05 10:35 | 59.895 | 250 MW trip. Frequency decayed to 59.95 prior to event. |

Deployed Responsive (19) (Reported Above)

| 12/1/05 17:40:18 | 12/12/05 6:02:02 |
| --- | --- |
| 12/1/05 22:06:18 | 12/13/05 5:00:14 |
| 12/3/05 18:02:42 | 12/13/05 13:33:30 |
| 12/3/05 21:18:16 | 12/13/05 22:03:30 |
| 12/4/05 17:39:12 | 12/15/05 6:11:14 |
| 12/5/05 6:10:16 | 12/15/05 7:16:28 |
| 12/7/05 20:26:54 | 12/16/05 7:05:04 |
| 12/8/05 6:05:30 | 12/17/05 22:13:14 |
| 12/8/05 12:02:22 | 12/23/05 4:02:34 |
| 12/8/05 17:57:24 | 12/30/05 18:51:22 |
| 12/9/05 17:11:42 | 12/31/05 10:35:30 |

Day Ahead Capacity Purchases

| Historical OOMC/RMR | Dec 04 | Nov 05 | Dec 05 |
| --- | --- | --- | --- |
| DFW | 17 | 8 | 34 |
| E RIO | 47 | 142 | 83 |
| W RIO | 49 | 39 | 63 |
| Laredo | 43 | 42 | 40 |
| Bryan Area | 17 | 29 | 18 |
| Corpus | 38 | 8 | 9 |
| Austin | 0 | 0 | 4 |
| North | 0 | 10 | 4 |
| Western | 14 | 7 | 18 |
| Houston | 0 | 3 | 0 |
| San Antonio | 1 | 61 | 24 |
| Northeast | 0 | 2 | 2 |
|  | 242 | 351 | 299 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overload | Days |
| --- | --- | --- |
| Dansby - Hearne 138kV | Hearn - Hearne Switch 69kV | 9 |
| Marion - Skyline - STP 345kV | Schertz-Parkway 138kV | 9 |
| Comanche Peak 1 & 2 | Uvalde - Asphalt Mines 138kV | 7 |
| Oklaunion | Stephenville - Lingleville 138kV | 6 |
| Marion - Zorn - Clear Spring 345kV | Seguin - Zorn 138kV | 5 |
| Benbrook - Parker & Graham 345kV | Stephenville - Lingleville 138kV | 4 |
| Comanche Peak - Decordova & Wolf Hollow - Rocky Creek 345kV | Concord 345kV/138kV Auto | 3 |
| Kendall - Fredericksburg 138kV | Kendall - Comfort 138kV | 3 |
| Asherton - West Conoco 138kV | Uvalde - Asphalt Mines 138kV | 2 |
| Comanche Peak 1 & 2 | Gideon - Butler 138kV | 2 |
| Dilley SW-North Laredo 138kV | North Laredo-Asherton 138kV | 2 |
| Graham - Benbrook - Parker 345kV | Stevenville-Lingeville 138kV | 2 |
| Hi Cross - Salem Walk 138kV | Burleson - Pedernales 138kV | 2 |
| Holt Switch - Andrews North 138kV | Holt Switch - Emma Tap 69kV | 2 |
| Marion - Hill Country 345kV | Schertz-Parkway 138kV | 2 |
| North Edinburg 345kV/138kV Auto | Rio Hondo - Magic Valley Burns 138kV | 2 |
| Trinidad - Watermill - Tricorner 345kV | TRSES 345kV/138kVAuto | 2 |
| Allen - Renner & Plano Tennyson 345kV | Allen Switch - Plano Alma Road 138kV | 1 |
| Austrop - Sandow 345kV | Gideon - Butler 138kV | 1 |
| Dansby T2 138kV/69kV Auto | Hearn - Hearne Switch 69kV | 1 |
| Denton 138kV/69kV T1 Auto | West Denton - Airport TMPP 138kV | 1 |
| Everman Switch - Decordova SES 345kV | Concord 345kV/138kV Autotransformer | 1 |
| Gibbons Creek - Bryan East 138kV | Atkins - Shady Lane 69kV | 1 |
| Hollly-Barney Davis 138kV | Mustang Island-Port Aransas 69kV | 1 |
| Kendall 345kV/138kV Auto | Ferguson - Gillespie 138kV | 1 |
| Laredo Plant - Falfurrias 138kV | San Diego - Freer 138kV | 1 |
| Lytton Spring - Zorn & Austrop - Zorn | San Marcos-Canyon 138kV | 1 |
| North Edinburg 345kV/138kV Auto | Weslaco - Heidelburg 138kV | 1 |
| Odessa EHV - Moss Sw 138kV | Olefin Sw - General Tire Sw | 1 |
| Pharr - Pharr MVEC 138kV | North Edinberg - Moore Field 69kV | 1 |
| Silas Ray - Military Highway 69kV | Airport 138kV/69kV Auto | 1 |
| STP - Skyline & Hill Country 345kV | Blessing - Lolita 138kV | 1 |
| Stryker - Trinidad 345kV | Athens Sw - Athens Tap 138kV | 1 |
| Holly - Airline 138kV | Aransas Pass - Seawall 69kV | 1 |
| Sandow - Austrop 345kV | Gideon - Butler LCRA 138kV | 1 |
| Sargent Road - Watermill 345kV | Cedar Hill 345kV/138kV Auto | 1 |

Zonal

South – Houston		1

South – North			9

North – West 			9

New RAP

- None

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 12/01/2005 | Power Operations Bulletin 230 | 230 |
| 12/01/2005 | T&S Desk - Maintenance Level 2 & 3 Outages | 229 |
| 12/01/2005 | T&S Desk - Block Load Transfer | 228 |
| 12/01/2005 | T&S Desk - Western Area Action Plan for Voltage Support | 227 |
| 12/01/2005 | FC Desk - DC Ties | 226 |
| 12/01/2005 | FC Desk - South DC Tie | 225 |

Blackout/Load Shed incidences

12/03   08:13   the following elements were lost:

- 138 kV bus at Live Oak

- 138/69 kV transformer at Live Oak

- the 69kV bus at Live Oak

- the Live Oak – Sonora 138kV line

- the Live Oak – Pave Paws SWTEC – San Angelo 138kV line

- the Live Oak – Pave Paws 69kV line

- the Live Oak – Eldorado 69kV

Sonora - City of Sonora 69kV line was out of service for a planned outage. This caused the load at City of Sonora to be fed radially through Eldorado.  As a result, load at the following stations were lost totaling 10 MW:

- City of Sonora

- Shell Bailey

- Eldorado

- Page Field

- Middle Valley

- Fort McKavett

A broken cross-arm and an insulator were found between Shell Bailey and City of Sonora.  The relays at Live Oak were reset and put back into service with no problems. All load and transmission elements were restored at 10:06.

12/8   20:14 	The Hamilton – Sonora 138kV line tripped carrying 73 MW. The reported cause was a broken cross arm resulting from galloping conductors. The loading on the Uvalde – Hamilton 138kV line increased from 76 MW to 149 MW, 137% of the elements 111 MVA dynamic rating.  At 20:17, loading on the Uvalde – Hamilton 138 kV line caused a failure at a sleeve. This left only one 69kV line Hamilton – Illinois #4 and the DC tie at Eagle Pass feeding the area’s 161 MW demand.  The DC tie locked out and the 69kV line tripped due to low voltage causing the loss of the 161 MW of load.

Prior to the event, a Transmission Emergency had been posted for this contingency/ overload pair.  The Asherton – West Conoco 138 kV planned maintenance limited the area import capability.  The local TO elected to begin restoration of this line as the cause and time to restore the other trips had not been determined.  Schedules were flowing on the local DC tie during this event.  Local generation that had been brought on line across evening peak but was ramped off line IE 20:00.

At 21:59 local generation came online in an attempt to restore power to the Del Rio area in accordance with the Black Start Plan provided in the Temporary Outage Action Plan for the Asherton – West Conoco 138kV line outage. By 22:33, the Amistad – Buena Vista – Del Rio – Hamilton Rd 138kV corridor was established and load was restored. At 00:38 on 12/09/05 the local units tripped while crews were trying to connect the 69kV line from Hamilton – Illinois #4 due to stabilization problems with the incremental load additions.

At 01:02 a BLT at Eagle Pass was established and the DC Tie was bypassed to maximize the load restoration. By 01:10 the 138kV bus at Eagle Pass was energized and by 01:30 the Eagle Pass City – Rosita Creek 138kV line was energized with about 40 MW of load restored.

At 02:55, one local unit was back on line and generating about 30 MW and by 02:57 the Amistad – Amistad Tap – Hamilton Rd 138kV line had been energized along with the Hamilton Rd – Illinois #4 69kV line. A second unit was started at 04:58.

By 03:00 the repairs on the Uvalde – Hamilton 138kV line had been completed. The line could not be put into service due to problems with one phase at Bracketville. At 05:13 a fly over of the Sonora – Hamilton Rd 138kV line detected a broken cross-arm on the Sonora – Hamilton Rd 138kV line.

At 08:17 restoration of the area began with the Uvalde – Hamilton Rd 138kV line energized followed by the Hamilton – Maverick 138kV line at 08:46, and the Hamilton – Del Rio – Buena Vista – Amistad 138kV corridor at 09:36.  At 18:58 the Asherton – West Conoco 138kV line was restored.  At 20:00 The Transmission Emergency for the Del Rio and Eagle Pass area ended as well as the Transmission Emergency for loss of Sonora – Hamilton Rd 138kV loads Uvalde – Asphalt Mines 138kV that was declared on 12/06/05. At 21:56 the Sonora – Hamilton Rd 138kV line was returned to service. At this time the entire transmission load of 161 MW (32,000 customers) was restored. Distribution load was completely restored around 14:00 on 12/10/05.

Major system voltage problems

Voltage Instructions

12/3	03:30	Two units in North Zone instructed to lower system voltage.

12/14	02:30	North Zone unit instructed to lower system voltage.

Corpus Christi RMR status summary

ERCOT has announced a need for a unit at Barney Davis for 2006.  Study results related to this decision are posted at the ERCOT Operations and System Planning data website under “Reliability Must-Run (RMR) Studies” folder ERCOTSempraRMRStudyFiles11152005.zip.

Major Computer Problems, Enhancements & Fixes

None

Communication

12/3	12:08 – 12:30	Portal not operable

12/6	11:45 – 12:30	ERCOT lost of frequency control and placed a QSE on constant frequency.  The cause of the failure was the migration of software that was expected to be transparent to ERCOT operating systems.  ERCOT EMMS support has investigated the event to identify necessary changes in their processes.

12/9      Held 05:45 interval.  Incorrect offset entered.

12/13	Held 10:30 interval.  10:00 fail over caused problems with the Hour Ahead study.

12/18	08:00 – 10:45	Multiple QSE having difficulty submitting schedules to ERCOT.  Problems were detected on the communication path and were corrected by the provider.

Update on New Generation

12/29 	3 combined cycle units totaling 620 MW commercially available in the North Zone.

ERCOT peak (Unofficial)

12/8 20:00	48,378

Alerts, OCN, and Emergency Notices

| Transmission |  |  |  |
| --- | --- | --- | --- |
| 2-Dec | Transmission Alert |  | Loss of Odessa - Moss Sw loads Oelfin Sw - General Tire |
| 6-Dec | Transmission Emergency |  | Loss of Sonora - Hamilton loads Uvalde - Asphalt Mines |
| 7-Dec | Transmission Emergency |  | Loss of Sonora - Hamilton loads Uvalde - Asphalt Mines |
| 8-Dec | Transmission Emergency |  | Loss of Sonora - Hamilton loads Uvalde - Asphalt Mines |
| 8-Dec | Transmission Alert |  | Loss of San Miguel 138/69 loads Derby Pearsall |
| 9-Dec | Transmission Emergency |  | Comfort Kendall 138 kV loading |
| 9-Dec | Transmission Emergency |  | Loss of Sonora - Hamilton loads Uvalde - Asphalt Mines |
| 9-Dec | Transmission Emergency |  | Del Rio area forced outages |
| Alert, Operating Condition Notice, and Advisory |  |  |  |
| 3-Dec | OCN | Insufficient capacity for hours 18:00 - 20:00 |  |
| 3-Dec | Alert | Insufficient capacity for hours 19:00 - 20:00 |  |
| 7-9-Dec | OCN | Issued OCN for winter storm |  |
| 7-8-Dec | Advisory | Issued Advisory for winter storm |  |
| 7-9-Dec | Alert | Issued Alert for winter storm |  |
| 21-Dec | OCN | Insufficient capacity for 01:00 on 12/22 |  |
| 22-Dec | OCN | Insufficient capacity for hours 08:00 - 10:00 |  |
| 31-Dec | OCN | Insufficient capacity for hours 09:00 - 13:00 |  |

Other

12/15   7:16	The Valley SPS armed due to loading on the Collin to Anna Sw line 75_A reaching the 1362 MVA rating.  The SPS owner has been contacted and confirmed that the SPS actuated at the correct level.   Line loading rose sharply the hour prior to the actuation and reached 90% loading.  The overload situation coincided with the planned clearance of line 90_a, Renner Switch to Carrollton Northwest 345 kV line.  Outage Coordination and Day Ahead studies with this outage modeled did not predict 75_A loading to exceed 80%.

12/25 18:10 	138 kV bus cleared in the San Angelo area, tripping 2 lines, the 138/69 kV transformer and 5 MW of load.  The load was restored by 19:30 and the transformer by 23:30.  The cause of the trip was reported as a bad lightning arrestor forcing out the transformer.