## Slide 1: Outstanding Issues & Action Items
Obligations to Honor Ancillary Services Commitments
Variable ERCOT Bias
Sign reversals of the Regulation Signal

## Slide 2: 1. 6.6.4 Obligations to Honor Ancillary Services Commitments
The Ancillary Service Obligations from the schedule submitted prior to the close of the Adjustment Period are binding commitments of the QSE to ERCOT. If ERCOT issues Resource-specific OOME or Resource-specific Balancing Energy Dispatch Instructions to a QSE that causes the QSE to be unable to Supply its Ancillary Service Obligation(s), the ERCOT shall issue a verbal Dispatch Instruction that:
(1) Relieves that QSE from having to provide the specific Ancillary Service(s) for specific intervals and the reason or,
(2) Retracts the Dispatch given to the QSE so that the QSE may come back into compliance with their Ancillary Service Obligation(s).

## Slide 3: Cat 2 & 4 deployments
The RRS deployment supersedes the Category 2 or 4 deployments
  VDI granted only if RRS was deployed
  VDI temporarily relieve them from their Category 2’s and 4’s During RRS deployment.

## Slide 4: 2. Variable ERCOT Bias
During ROS discussions on PRR 586, ERCOT was requested to investigate implementing a variable bias.
ERCOT Bias calculated by averaging observed performance of Measurable Events over 2 periods
  May 1st to September 30th
  October 1st to April 30th

## Slide 5: Alternative Options Considered
Sum QSE telemetered bias
Estimate Bias based on unit mix
Average Bias over smaller periods
    Any significant variance in the bias term requires additional tuning of other parameters. A bias that could change with system conditions would be difficult to maintain

## Slide 6: 1. Sum QSE telemetered bias
QSE required to telemeter frequency bias of portfolio generation resources in accordance with Protocols § 6.5.1.1
  The sum of individual bias does not reflect total performance
    Most bias values provided are fairly accurate
    Some QSE currently are not submitting a bias value.
    Data failure could lead to wide variances in ERCOT bias

## Slide 7: 2. Estimate Bias based on unit mix
Build logic in EMMS that varies bias based on unit type and generic droop for each type.
  Actual droop characteristic unknown
  Available capacity (unit at HSL or LSL) changes actual individual response.
  Data failure could lead to wide variances in ERCOT bias
  Any significant variance in the bias term requires additional tuning of other parameters.

## Slide 8: 3. Average Bias over smaller periods
Change Monthly based on previous performance
  Reduces sample set
    May need 3+ years of response to have adequate number of Measurable events
    Rolling average would encompass peak and off-peak conditions

## Slide 9: Current Bias Setting
Although the bias term is static, ERCOT AGC adjusts the amount of control over different system conditions in 2 ways:
  Magnitude of frequency deviation
      Small deviations ~ bias/3
      Medium deviations ~ bias/2
  Operator action

## Slide 10: Frequency Desk Procedures
Adjustment of Requested ACE %
Allows operator to scale bias
  Control = ACE% * |bias*ΔF|
Normally set to 100%. Procedures direct operator to adjust the setting to
  Prevent Oscillation or under control (2.5.1 (1))
  Maintaining ERCOT CPS > 100 (2.4.3 (1))

## Slide 11: 3. Reversals of the Regulation Signal
ROS FCTF indicated counting the times the Regulation signal changed direction may be valuable in evaluating secondary frequency control
3 months data collected
1/8/06 18:30 – 20:30
  514 reversals over the day, 56 over the 2 hours.

## Slide 13: Summary
 | August | October | December
minimum | 363 | 370 | 357
maximum | 926 | 1036 | 1102
average | 496 | 682 | 608
stddev | 132 | 129 | 176