## Sheet1
Section 5 Protocols Clarification |  |  |  | 0 | 1
Reviewer | Section | Requested Clarification | TPTF 020606 Feedback | 0 | 2
Jay Dondeti | 5.5.1 (7) | What is the role of bus voltage limit violations in RUC? ERCOT believes that this voltage monitoring is not intended for RUC, but is a vestige from the real-time network analysis. If a voltage violation is expected in the day ahead it must be Represented as generic thermal constraint in RUC. If we are incorrect, please explain. |  | 5 | 1 | 7
Jay Dondeti & Sai Moorty | 5.5.1 | It is not clear how NSA will solve if the COP does not match the demand as forecasted by LF. It seems like we need an initial UC that ensures power balance before evaluating network security. Open loop between NSA and RUC or iterative loop between NSA and RUC. The diagram of security sequence or the description does not talk about multiple iterations between RUC and SFT. How is that handled? |  | 5 | 1
Jay Dondeti & Sai Moorty | 5.5.1 | Why is DRUC (normal) and HRUC (current) start from different breaker status? If the outages, both the ones going out of service and the ones coming in to services, are properly applied to each time point of RUC then starting from current breaker status for both DRUC and HRUC should be fine. Bullet item 2 states to use current status for HRUC and normal status for DRUC. Does that mean for HRUC after the first hour, Normal status will be used or else what? Appears that 5.5.1 (3) and 5.5.2 (9) (a) are inconsistent. |  | 5 | 1
John Adams | 5.5.1 (7) (a) | Perform full AC analysis of all contingencies. Based on its experience ERCOT is not confident it will be able to achieve high availability of this application using an AC power flow. Suggest DC power flow for RUC