| OGRR Number | 172 | OGRR Title | Special Protection System Obligations |
| --- | --- | --- | --- |
| Operating Guide Section Requiring Revision |  | 7.2.2, Design and Operating Requirements for ERCOT System Facilities |  |
| Protocol Section Requiring Revision, if any. |  | ## None |  |
| Revision Description |  | The changes permit the sharing of limited TDSP operating information with Generation Entities subject to SPS control as necessary to avoid SPS operations. The changes also propose differences in the SPS review and approval process between new SPSs that involve Generation Entities or affect a wide area, and other SPSs. |  |
| ###### Reason for Revision |  | The avoidance of unnecessary SPS operations justifies the sharing of operating information that might otherwise be viewed as potentially market sensitive. Some highly local SPSs (e.g., series reactor insertion or existing SPS settings modifications) should not have to complete the full ERCOT SPS review and approval process before being placed in service. |  |
| Timeline |  |  |  |
| Date Posted |  | 7/28/05 |  |
| Please see the Master List on the ERCOT website for current timeline information. |  |  |  |

| Sponsor |  |
| --- | --- |
| Name | Lee Westbrook |
| E-mail Address | lwestbrook@txued.com |
| Company | TXU Electric Delivery |
| Company Address | 2233-B Mountain Creek Pkwy |
| Phone Number | 214-743-6823 |
| Fax Number | 972-263-6710 |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | None |  | Process improvement |
| MARKET SEGMENT | None |  | Potential congestion reduction |
| Consumer | None |  | See Market Segment |
| LSE: General, Including NOIE | None |  | See Market Segment |
| LSE: CR & REP | None |  | See Market Segment |
| QSE | None |  | See Market Segment |
| Resource | Small potential impact |  | See ERCOT |
| TDSP | Small potential impact |  | See ERCOT |

Proposed Operating Guide Language Revision

### 7.2.2	Design and Operating Requirements for ERCOT System Facilities

1.	Protective relay system shall be designed to provide reliability, a combination of dependability and security, so that protective relay system will perform correctly to remove faulted equipment from the ERCOT System.

2.	For planned ERCOT System conditions, protective relay system shall be designed not to trip for stable swings which do not exceed the steady-state stability limit.  Note that when out-of-step blocking is used in one location, a method of out-of-step tripping should also be considered.  Protective relay system shall not interfere with the operation of the ERCOT System under the procedures identified in the other Operating Guides.

3.	Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

4.	The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even under first-contingency conditions.

5.	Applicable IEEE/ANSI guides shall be considered when applying the protective relay system on the ERCOT System.

6.	The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to this guide or to accepted IEEE/ANSI practice, then the Facility owners affected shall negotiate a solution.

7.	All Facility owners shall give sufficient advance notice to ERCOT of any changes to their Facilities that could require changes in the protective relay system of neighboring Facility owners.

8.	Facility owner’s operations personnel shall be familiar with the purposes and limitations of the protective relay system.

9.	The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility owner to ensure that the protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Where redundant protective relay systems are required, separate AC current inputs and separately fused DC control voltages shall be provided with the upgraded protective relay system.  Documentation of the review shall be maintained and supplied by the Facility owner to ERCOT or NERC on their request within 30 days.  This documentation shall be reviewed by ERCOT for verification of implementation.

10.	Upon ERCOT’s request, within 30 days, PGCs shall provide ERCOT with the operating characteristics of any generator’s equipment protective relay system or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

11.	Upon ERCOT’s request, within 30 days, Generation Entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and the protective relay system.

12.	Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Documentation of coordination shall be supplied, by Generation Entities, to ERCOT upon their request within 30 days.

13.	Special Protection Systems (SPS) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable ERCOT System performance.  SPS actions include among others, changes in demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable Facility loadings.  A Type 1 SPS is any SPS that has wide-area impact and specifically includes any SPS that a) is designed to alter generation output or otherwise constrain generation, or b) is designed to open 345 kV transmission lines or other lines that interconnect TDSPs and impact transfer limits.  Any SPS that has only local-area impact and involves only the Facilities of the owner-TDSP is a Type 2 SPS.  Any SPS not determined by ERCOT to be a Type 1 SPS is a Type 2 SPS.  Any SPS, whether Type 1 or Type 2, shall meet all requirements of NERC Standards relating to SPSs, and shall additionally meet the following ERCOT requirements::

- The SPS owner shall coordinate design and implementation of the SPS with the owners and operators of Facilities included in the SPS.

- The SPS shall be automatically armed when appropriate.

- The SPS shall not operate unnecessarily.  Whenever operating information available to the SPS owner can be used by the owner of Generation Resources that are part of the SPS to manage the Dispatch of those Generation Resources so as to avoid operation of the SPS, such information may be provided to the Generation Resource owner by the SPS owner.

- The status indication of any automatic or manual arming of the SPS shall be provided as SCADA alarm inputs.

- The SPS shall be designed in accordance with the intent of this Operating Guide when they are required to prevent adverse effects outside the local area.

- When a Transmission Operator (TO) removes a SPS from service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the unavailability of the SPS.  When a SPS is returned to service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

14.	The owner(s) of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

- ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS every five years, or sooner as required by changes in system conditions.  Each review shall proceed according to a timetable documented in ERCOT Procedures and posted on the ERCOT website.

- For a proposed Type 1 SPS, the review must be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Service Request to ERCOT.

- For a proposed Type 2 SPS, the SPS may be placed into service before completion of the ERCOT review, with advanced prior notice to ERCOT in the form of a Service Request.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  Existing SPSs that have already undergone at least one review shall remain in service during any subsequent review, and proposed modifications to existing SPSs may be implemented, upon notice to ERCOT, before completion of the required ERCOT review.

- Times to place SPS into service must be coordinated and provide sufficient time to get the SPS into the monitoring system prior to their being in service.

- An ERCOT SPS review shall verify that the SPS complies with ERCOT and NERC criteria and guides.  The review shall evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required.  The review shall also evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, and without any other system contingency.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within thirty (30) days.

- As part of the ERCOT review, the appropriate ROS working groups such as the Steady State Working Group, the Dynamics Working Group, and/or the System Protection Working Group shall review the SPS and report any comments, questions, or issues to ERCOT for resolution. ERCOT may work with owner(s) as necessary to address all issues.

- ERCOT shall develop a methodology to include the SPS in the Total Transfer Capability (TTC) calculations, if appropriate.

- ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.

15.	SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report located in Section 6 of these Operating Guides.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures. If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.

16.	For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the ERCOT website. Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, using a Service Request, whenever the SPS  is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT.