| OGRR Number | 172 | OGRR Title | Special Protection System Obligations |  |
| --- | --- | --- | --- | --- |
| Timeline (Normal or Urgent) | Normal | Action |  | Approved |
| Operating Guide Section(s) Requiring Revision (include Section No. and Title) |  | 7.2.2, Design and Operating Requirements for ERCOT System Facilities |  |  |
| Effective Date |  | April 1, 2006 |  |  |
| Protocol Section(s) Requiring Revision, if any |  | None. |  |  |
| Revision Description |  | The proposed changes permit the sharing of limited TDSP operating information with Generation Entities subject to Special Protection System (SPS) control as necessary to avoid SPS operations. The changes also propose differences in the SPS review and approval process between new SPSs that involve Generation Entities or affect a wide area, and other SPSs. |  |  |
| Overall Market Benefit |  | Potential congestion reduction |  |  |
| Overall Market Impact |  | Change to SPS process |  |  |
| Consumer Impact |  | None |  |  |
| Procedural History |  | - On 7/28/05, OGRR172 was posted. - On 8/26/05, Calpine posted comments. - On 10/5/05, TXU ED posted comments. - On 10/17/05, Centerpoint posted comments. - On 10/19/05, OWG considered OGRR172. - On 11/10/05, ROS considered OGRR172. - On 12/1/05, ERCOT posted the Impact Analysis (IA). - On 1/13/06, ROS reviewed the IA. - On 2/23/06, PRS reviewed OGRR172. - On 3/9/06, TAC reviewed OGRR172. |  |  |
| OWG Recommendation |  | OWG recommended approval of OGRR172 as revised by Centerpoint comments. |  |  |
| Summary of OWG Discussion |  | No discussion. |  |  |
| ROS Recommendation |  | ROS voted unanimously to recommend approval of OGRR172 as recommended by OWG. All market segments were present for the vote. |  |  |
| Summary of ROS Discussion |  | No discussion. |  |  |

| PRS Consistency Determination | No PRS member noted a discrepancy between OGRR172 and the Protocols. |
| --- | --- |
| TAC Action | TAC voted unanimously to approve OGRR172 as recommended by ROS. All market segments were present for the vote. |

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | None |  | Process improvement |
| MARKET SEGMENT |  |  |  |
| Consumer | None |  | Potential congestion reduction |
| LSE: General, Including NOIE | None |  | Potential congestion reduction |
| LSE: CR & REP | None |  | Potential congestion reduction |
| QSE | None |  | Potential congestion reduction |
| Resource | Small potential impact |  | Process improvement |
| TDSP | Small potential impact |  | Process improvement |

| Original Sponsor |  |
| --- | --- |
| Name | Lee Westbrook |
| Company | TXU Electric Delivery |
| Segment | Investor Owned Utility |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| Calpine | Asserted that all SPSs that involve DC Tie schedule flows be treated as resources, in accordance with the existing Protocols and offered revised language |
| TXU Electric Delivery | Offered revised language on behalf of the OGRTF. |
| Centerpoint | Proposed revising the definition of SPS in Section 7.2.2 -13 to explicitly exclude under-voltage and under-frequency load shedding as consistent with the NERC definition. |

Proposed Operating Guide Language Revision

### 7.2.2	Design and Operating Requirements for ERCOT System Facilities

1.	Protective relay system shall be designed to provide reliability, a combination of dependability and security, so that protective relay system will perform correctly to remove faulted equipment from the ERCOT System.

2.	For planned ERCOT System conditions, protective relay system shall be designed not to trip for stable swings which do not exceed the steady-state stability limit.  Note that when out-of-step blocking is used in one location, a method of out-of-step tripping should also be considered.  Protective relay system shall not interfere with the operation of the ERCOT System under the procedures identified in the other Operating Guides.

3.	Any loading limits imposed by the protective relay system shall be documented and followed as an ERCOT System operating constraint.

4.	The thermal capability of all protection system components shall be adequate to withstand the maximum short time and continuous loading conditions to which the associated protected elements may be subjected, even under first-contingency conditions.

5.	Applicable IEEE/ANSI guides shall be considered when applying the protective relay system on the ERCOT System.

6.	The planning and design of generation, transmission and substation configurations shall take into account the protective relay system requirements of dependability, security and simplicity.  If configurations are proposed that require protective relay systems that do not conform to this guide or to accepted IEEE/ANSI practice, then the Facility owners affected shall negotiate a solution.

7.	All Facility owners shall give sufficient advance notice to ERCOT of any changes to their Facilities that could require changes in the protective relay system of neighboring Facility owners.

8.	Facility owner’s operations personnel shall be familiar with the purposes and limitations of the protective relay system.

9.	The design, coordination, and maintainability of all existing protective relay systems shall be reviewed periodically by the Facility owner to ensure that the protective relay systems continue to meet ERCOT System requirements.  This review shall include the need for redundancy.  Where redundant protective relay systems are required, separate AC current inputs and separately fused DC control voltages shall be provided with the upgraded protective relay system.  Documentation of the review shall be maintained and supplied by the Facility owner to ERCOT or NERC on their request within 30 days.  This documentation shall be reviewed by ERCOT for verification of implementation.

10.	Upon ERCOT’s request, within 30 days, PGCs shall provide ERCOT with the operating characteristics of any generator’s equipment protective relay system or controls that may respond to temporary excursions in voltage, frequency, or loading with actions that could lead to tripping of the generator.

11.	Upon ERCOT’s request, within 30 days, Generation Entities shall provide ERCOT with information that describes how generator controls coordinate with the generator’s short-term capabilities and the protective relay system.

12.	Over-excitation limiters, when used, shall be coordinated with the thermal capability of the generator field winding.  After allowing temporary field current overload, the limiter shall operate through the automatic AC voltage regulator to reduce field current to the continuous rating.  Return to normal AC voltage regulation after current reduction shall be automatic.  The over-excitation limiter shall be coordinated with the over-excitation protection so that over-excitation protection only operates for failure of the voltage regulator/limiter.  Documentation of coordination shall be supplied, by Generation Entities, to ERCOT upon their request within 30 days.

13.	Special Protection Systems (SPS) are protective relay systems designed to detect abnormal ERCOT System conditions and take pre-planned corrective action (other than the isolation of faulted elements) to provide acceptable ERCOT System performance.  SPS actions include among others, changes in demand, generation, or system configuration to maintain system stability, acceptable voltages, or acceptable Facility loadings.  An SPS does not include underfrequency or undervoltage load shedding.  A Type 1 SPS is any SPS that has wide-area impact and specifically includes any SPS that a) is designed to alter generation output or otherwise constrain generation or imports over DC Ties, or b) is designed to open 345 kV transmission lines or other lines that interconnect TDSPs and impact transfer limits.  Any SPS that has only local-area impact and involves only the Facilities of the owner-TDSP is a Type 2 SPS.  The determination of whether an SPS is Type 1 or Type 2 will be made by ERCOT upon receipt of a description of the SPS from the SPS owner.  Any SPS, whether Type 1 or Type 2, shall meet all requirements of NERC Standards relating to SPSs, and shall additionally meet the following ERCOT requirements::

- The SPS owner shall coordinate design and implementation of the SPS with the owners and operators of Facilities included in the SPS, including but not limited to Generation Resources and HVDC ties.

- The SPS shall be automatically armed when appropriate.

- The SPS shall not operate unnecessarily.  To avoid unnecessary SPS operation, the SPS owner may provide a real-time status indication to the owner of any Generation Resource controlled by the SPS to show when the flow on one or more of the SPS’s monitored facilities exceeds 90% of the flow necessary to arm the SPS. The cost necessary to provide such status indication shall be allocated as agreed by the SPS owner and the Generation Resource owner.

- The status indication of any automatic or manual arming of the SPS shall be provided as SCADA alarm inputs to the owners of any facility(ies) controlled by the SPS.

- When a Transmission Operator (TO) removes a SPS from service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the unavailability of the SPS and notify the Market.  When a SPS is returned to service, the TO shall immediately notify ERCOT operations.  ERCOT shall modify its reliability constraints to recognize the availability of the SPS.

14.	The owner(s) of an existing, modified, or proposed SPS shall submit documentation of the SPS to ERCOT for review and compilation into an ERCOT SPS database.  The documentation shall detail the design, operation, functional testing, and coordination of the SPS with other protection and control systems.

- ERCOT shall conduct a review of each proposed SPS and each proposed modification to an existing SPS.  Additionally, it shall conduct a review of each existing SPS every five years, or sooner as required by changes in system conditions.  Each review shall proceed according to a process and timetable documented in ERCOT Procedures and posted on the ERCOT website.

- For a proposed Type 1 SPS, the review must be completed before the SPS is placed in service, unless ERCOT specifically determines that exemption of the proposed SPS from the review completion requirement is warranted.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  The implementation schedule must be confirmed through submission of a Service Request to ERCOT.

- For a proposed Type 2 SPS, the SPS may be placed into service before completion of the ERCOT review, with advanced prior notice to ERCOT in the form of a Service Request.  The timing of placing the SPS into service must be coordinated with and approved by ERCOT.  Existing SPSs that have already undergone at least one review shall remain in service during any subsequent review, and proposed modifications to existing SPSs may be implemented, upon notice to ERCOT, and approval of ERCOT before completion of the required ERCOT review.

- The process and schedule for placing an SPS into service must be consistent with documented ERCOT Procedures.  The schedule must be coordinated among ERCOT and the owners of any facility(ies) controlled by the SPS, and shall provide sufficient time to perform any necessary testing prior to its being placed in service.

- An ERCOT SPS review shall verify that the SPS complies with ERCOT and NERC criteria and guides.  The review shall evaluate and document the consequences of failure of a single component of the SPS, which would result in failure of the SPS to operate when required.  The review shall also evaluate and document the consequences of misoperation, incorrect operation, or unintended operation of an SPS, when considered by itself, and without any other system contingency.  If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.  The current review results shall be kept on file and supplied to NERC on request within thirty (30) days.

- As part of the ERCOT review and unless judged to be unnecessary by ERCOT, the appropriate ROS working groups such as the Steady State Working Group, the Dynamics Working Group, and/or the System Protection Working Group shall review the SPS and report any comments, questions, or issues to ERCOT for resolution. ERCOT may work with the owner(s) of facilities controlled by the SPS as necessary to address all issues.

- ERCOT shall develop a methodology to include the SPS in the Commercially Significant Constraint (CSC) limit calculations, if appropriate.

- ERCOT’s review shall provide an opportunity for and include consideration of comments submitted by Market Participants affected by the SPS.

15.	SPS owners shall notify ERCOT of all SPS operations.  Documentation of SPS failures or misoperations shall be provided to ERCOT using the Relay Misoperation Report located in Section 6 of these Operating Guides.  ERCOT shall conduct an analysis of all SPS operations, misoperations, and failures. If deficiencies are identified, a plan to correct the deficiencies shall be developed and implemented.

16.	For each SPS, the owner shall either identify a preferred exit strategy or explain why no exit strategy is needed to ERCOT.  This shall take place according to a timetable documented in ERCOT Procedures and posted on the ERCOT website. Once an exit strategy is complete and a SPS is no longer needed, the owner of an existing SPS shall notify ERCOT, using a Service Request, whenever the SPS  is to be permanently disabled, and shall do so according to a timetable coordinated with and approved by ERCOT and the owners of all facilities controlled by the SPS.