| PRR Number | 630 | PRR Title | Private Use Networks |  |
| --- | --- | --- | --- | --- |
| Timeline (Normal or Urgent) | Normal | Recommended Action |  | Approval |
| Protocol Section(s) Requiring Revision (include Section No. and Title) |  | 2.1 – Definitions 5.2.1 – Standards and Practices 5.2.2 – Operating Standards 6.5.7 – Voltage Support Service |  |  |
| Proposed Effective Date |  | April 1, 2006 |  |  |
| Priority and Rank Assigned |  | N/A |  |  |
| Revision Description |  | This PRR would add a requirement for Private Use Networks (i.e., those networks that are connected to the ERCOT system that may include both generation and Load “behind the meter”) to maintain and report appropriate watt/VAR metering data at each substation, identical to the requirements of Distribution Service Providers (DSPs), and would require reporting of addition or deletion of Load points. |  |  |
| Overall Market Benefit |  | Improved system reliability by requiring Private Use Networks to meet the same power factor and voltage standards required of other Market Participants. |  |  |
| Overall Market Impact |  | Would place additional reporting requirements on certain Private User Networks. |  |  |
| Consumer Impact |  | None. |  |  |
| Credit Impacts: Has the Credit Workgroup reviewed the PRR? If so, are there credit impacts? (indicate Yes or No, and if Yes, include a summary of impact) |  | Yes. ERCOT credit staff and the CWG have reviewed PRR630 and do not believe that it requires changes to credit monitoring activity or the calculation of liability. |  |  |
| Procedural History |  | - PRR630 was posted on 08/26/05. - On 9/9/05, Brazos Valley Electric Coop (Brazos) posted comments. - On 9/15/05, CenterPoint Energy (CNP) posted comments. - On 12/16/05, PRS considered PRR630. - On 12/19/05, Texas Industrial Energy Consumers (TIEC) posted comments to this PRR. - On 1/7/06, ERCOT posted the Impact Analysis (IA) for this PRR. - On 1/17/06, ERCOT posted comments. - On 1/25/06 CNP posted comments. - On 1/19/06, PRS reviewed the IA, ERCOT’s comments and PRS Recommendation Report for PRR630. - On 2/2/06, TAC considered this PRR. - On 3/1/06, the PRR630 Taskforce (TF) posted comments. - On 3/9/06, TAC again considered this PRR. |  |  |
| PRS recommendation (indicate whether all segments were present for the vote, and the segment of parties that voted no or abstained) |  | On 12/16/2005, PRS voted to recommend approval of PRR630 as modified by Centerpoint’s comments. The motion passed with two opposing votes from the Consumers and Independent REPs and two abstentions from the Investor Owned Utilities and the Independent Generators. All market segments were present. On 01/19/06, PRS voted to recommend approval of PRR630 as modified by ERCOT comments and PRS, and endorse the PRS Recommendation Report and Impact Analysis with three abstentions from the Consumer (2) and Independent Power Marketer (1) segments. All market segments were present. |  |  |
| Summary of PRS discussion |  | On 12/16/05, PRS members agreed that PRR630 addresses only the power factor for Private Use Networks and does not address issues related to reserve requirements. Participants also discussed existing PUCT requirements, the pro-forma tariffs, and possible unintended consequences of this PRR. On 01/19/06, PRS discussed ERCOT’s comments and the requirements for Private Use Networks. |  |  |
| TAC recommendation (indicate whether all segments were present for the vote, and the segment of parties that voted no or abstained) |  | On 3/9/06, TAC voted to recommend approval of this PRR as revised by the PRR630 TF comments and TAC. The vote was unanimous with all market segments present. |  |  |
| Summary of TAC discussion |  | On 2/9/06, TAC tabled discussion of this PRR pending resolution of Consumer objections by the PRR630 TF. There was no discussion on 3/9/06. |  |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

| Assumptions | 1 | No impact to ERCOT. |  |
| --- | --- | --- | --- |
|  |  | Impact Area | Monetary Impact |
| Market Cost | 1 | Will add reporting requirements and power factor and voltage standards for certain Private Use Networks. | Unknown |
|  |  | Impact Area | Monetary Impact |
| Market Benefit | 1 | Improved system reliability by requiring Private Use Networks to meet the same power factor and voltage standards required of other Market Participants. | Unknown |
| Additional Qualitative Information | 1 | None |  |
| Other | 1 | None |  |
| Comments | 2 |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | Henry Durrwachter |
| Company | Investor Owned Utility |
| Market Segment | TXU Wholesale |

| Comments Received |  |
| --- | --- |
| Comment Author | Comment Description |
| Brazos 090905 | Questioned the definition of Private Use Network. |
| CenterPoint 091505 | Agreed with the concept of this PRR and proposed additional language modifications. |
| TIEC 121605 | Recommended Rejection of this PRR. |
| ERCOT 011706 | Provided clarifying language for PRR630. |
| CenterPoint 012506 | Offered revisions to clearly identify the TDSP’s responsibility when a power factor requirement is defined by a TDSP’s tariff. |
| PRR630 TF 030106 | Offered revised consensus language. |

Proposed Protocol Language Revision

  - Definitions

- Private Use Network

An electric network connected to the ERCOT Transmission Grid that contains load that is not directly metered by ERCOT (i.e., load that is typically netted with internal generation).

# 5.2.1	Standards and Practices

Each TSP,  DSP, and Private Use Network must meet the requirements specified in Section 5.2.1, Standards and Practices, or at their option, meet alternative requirements specifically approved by ERCOT.  Such alternative requirements may include requirements for aggregated groups of Facilities.

(1)	Sufficient static Reactive Power capability shall be installed by a DSP or a Private Use Network not subject to a TDSP tariff  in substations and on the distribution voltage system to maintain at least a ninety-seven hundredths (0.97) lagging power factor for the maximum net active power supplied from a substation transformer at its distribution voltage terminals to the distribution voltage system. In those cases where a Private Use Network’s power factor is established and governed by a TDSP tariff, the TDSP and Private Use Network owner shall ensure that the Private Use Network meets the requirements as defined and measured in the applicable tariff.  For any substation transformer serving multiple DSPs, this power factor requirement shall be applied to each DSP individually for its portion of the total Load served.

(2)	Annually, ERCOT will review DSP power factors using the actual summer Load and power factor information included in the annual load data request to assess whether DSPs comply with the requirements of Section 5.2.1, Standards and Practices.  All DSP substations whose annual peak Load has exceeded ten (10) MW shall have and maintain Watt/VAR metering sufficient to monitor compliance; otherwise, DSPs will not be required to install additional metering to determine compliance.  At times selected by ERCOT, ERCOT will require manual power factor measurement at substations and points of interconnection that do not have power factor metering.  ERCOT will endeavor to provide DSPs sufficient notice to perform the manual measurements.  Such requests shall be limited to four (4) times per calendar year for each DSP substation or point of interconnection where power factor measurements are not available.

(3)	All DSPs shall report any changes in their estimated net impact on ERCOT as part of the annual Load data assessment.

(4)	As part of the annual Load-data-assessment, all Resource Entities owning Generation Resources shall provide an annual estimate of the highest potential affiliated MW and MVAR load (including any load netted with the generation output) and the highest potential MW and MVAR generation that could be experienced at the point of interconnection to the ERCOT Transmission Grid, based on the then current configuration (and the projected configuration if the configuration is going to change during the year) of the Generation Resource and any affiliated loads.

(5)	If actual conditions indicate probable non-compliance, ERCOT will require power factor measurements at the time of its choice while providing sufficient notice to perform the measurements.

(6)	Assuming optimal use of all other required installed Reactive Power capability, ERCOT Regional Planning Groups or Transmission Planning shall determine and demonstrate the need for any additional static and/or dynamic Reactive Power capability necessary to ensure compliance with the ERCOT Planning Criteria, and ERCOT Transmission Planning shall establish responsibility for any associated Facility additions among ERCOT TSPs.

(7)	For monitoring of compliance of the TSP's planned Facilities to the ERCOT Planning Criteria performance requirements, a self-certification process with random audits (similar to compliance to NERC Planning Standards), in conjunction with work performed in the ERCOT Regional Planning Groups, shall be used.  Except under Force Majeure conditions, if a TSP fails to maintain transmission system voltage within two percent (2%) of the scheduled voltage while reactive sources under its direct control are not fully utilized, ERCOT may, at its discretion, report this to the ERCOT Compliance Office.

(8)	The ERCOT Compliance Office will investigate claims of alleged non-compliance using ERCOT compliance procedures.  The ERCOT Compliance Office will use its compliance procedures to address confirmed non-compliance situations.  The ERCOT Compliance Office will advise ERCOT and TSP planning and operating staffs of the results of such investigations.

5.2.2	Operating Standards

ERCOT, and TDSPs shall operate the ERCOT System in compliance with Good Utility Practice and NERC and ERCOT standards, policies, guidelines and operating procedures.  These Protocols shall control to the extent of any inconsistency between the Protocols and any of the following documents:

(1)	Any reliability guides applicable to ERCOT, including the Operating Guides;

(2)	The NERC Operating Manual and ERCOT procedures manual, supplied by NERC and ERCOT, respectively, as references for dispatchers to use during normal and emergency operations of the ERCOT Transmission Grid;

(3)	Specific operating procedures, submitted to ERCOT by individual transmission Facility owners or operators to address operating problems on their respective grids that could affect operation of the interconnected ERCOT Transmission Grid; and

(4)	Guidelines established by the ERCOT Board, which may be more stringent than those established by NERC for the secure operation of the ERCOT System.

6.5.7	Voltage Support Service

All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than twenty (20) MVA or those units connected to the same transmission bus that have gross generating unit ratings aggregating to greater than twenty (20) MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service.