| OGRR Number | 179 |  | OGRR Title | Under-Voltage Load Shedding Protection Systems |  |
| --- | --- | --- | --- | --- | --- |
| Timeline (Normal or Urgent) |  | Normal | Recommended Action |  | Approval |
| Operating Guide Section Requiring Revision |  |  | 7.2.5.3, Specific Application Considerations |  |  |
| Protocol Section Requiring Revision, if any. |  |  | ## None |  |  |
| Proposed Effective Date |  |  | ## June 1, 2006 |  |  |
| Revision Description |  |  | Clarifies requirements for under-voltage Load shedding protection systems and minor modifications for references to supporting Sections of the Operating Guide (regarding protection system maintenance). |  |  |
| ###### Reason for Revision |  |  | To satisfy ERCOT requirements relating to under-voltage Load shedding implementation by individual utilities. |  |  |
| ###### Overall Market Benefit |  |  | Clearer language in Operating Guides. |  |  |
| ###### Overall Market Impact |  |  | None. |  |  |
| ###### Consumer Impact |  |  | None. |  |  |
| ###### Procedural History |  |  | - On 1/5/06, OGRR179 was posted. - On 3/17/06, ERCOT posted comments. - On 3/22/06, OWG reviewed the OGRR. |  |  |
| ###### OWG Recommendation |  |  | On 3/22/06, OWG recommended approval of OGRR179 as revised by ERCOT comments and OGRTF. |  |  |
| ###### Summary of OWG Discussion |  |  | On 3/22/06, ERCOT explained that its revision was made to ensure that load protection systems act before protective relays for generators. OWG verified that the protective relay requirements are contained in Section 3.1.4.6. |  |  |

| Original Sponsor |  |
| --- | --- |
| Name | Mehrdad Vatani, Chair, on behalf of the System Protection Working Group |
| Company | N/A |
| Market Segment | N/A |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

|  | Impact |  | Benefit |
| --- | --- | --- | --- |
|  | Business | Computer Systems |  |
| ERCOT | None | None | Operating Guides clearer and more accurate |
| MARKET SEGMENT |  |  |  |
| Consumer | None | None | Operating Guides clearer and more accurate |
| LSE: General, Including NOIE | None | None | Operating Guides clearer and more accurate |
| LSE: CR & REP | None | None | Operating Guides clearer and more accurate |
| QSE | None | None | Operating Guides clearer and more accurate |
| Resource | None | None | Operating Guides clearer and more accurate |
| TDSP | None | None | Operating Guides clearer and more accurate |

Proposed Operating Guide Language Revision

#### 7.2.5.3	Specific Application Considerations

Automatic Under-Frequency Load Shedding Protection Systems

- Automatic under-frequency Load shedding systems are classified as protective relay systems.  The maintenance requirements, discussed in Section 7.2.4, apply to under-frequency Load shedding protection systems as well.

- 1.	Automatic under-frequency Load shedding systems are generally located on equipment operated below 60 kV; however, they have a direct effect on the operation of the system during major emergencies.

- 2.	The criteria for the operation of these protection systems are detailed in Operating Guide 2.9  - Requirements for Under-Frequency Relaying.

- 3.	Automatic under-frequency Load shedding protection systems need not be duplicated.

- 4.	Generator and turbine under-frequency protection systems shall be coordinated with Operating Guide 2.9 - Requirements for Under-Frequency Relaying.

- 5.	On pressurized water reactor steam supply units where under-frequency related protection systems are installed to detect loss of coolant flow condition, these protection systems shall be coordinated with the automatic under-frequency load shedding program.

- 6.	Automatic Load restoration for a UFLS operation is not currently utilized in ERCOT.

Automatic Under-Voltage Load Shedding Protection Systems

Automatic under-voltage Load shedding systems are classified as protective relay systems. The maintenance requirements, discussed in Section 7.2.4, apply to under-voltage Load shedding protection systems as well.

- 1.	The requirement for under-voltage relaying shall be determined by system studies performed / administered by ERCOT designated working groups or equipment owners. The system studies should indicate the following:

- Amount of Load to be shed to restore voltage to minimum acceptable level or higher,

- The minimum and maximum time delay allowed before automatically shedding Load,

- The voltage level(s) at which to initiate automatic relay operation, and

- The location(s) for effectively applying under-voltage Load shedding protection systems.

- 2.	Automatic under-voltage Load shedding protection systems need not be duplicated.

- 3.	Analyses shall be performed on undervoltage load shedding schemes by working groups and/or equipment owners as assigned by ERCOT to demonstrate that they are expected to act before generators trip Off-line due to the protective relay requirements described in Section 3.1.4.6, Protective Relaying Requirement.  A specific exemption from this analysis requirement may be provided by the ERCOT Reliability Operatiions Subcommittee (ROS).

- 4.	Under-voltage protection systems shall be designed to coordinate with other protective devices and control schemes during momentary voltage dips, sustained faults, low voltages caused by stalled motors, motor starting, etc.

- 5.	Automatic Load restoration for a UVLS operation is not currently utilized in ERCOT.

- 6.	The scheme shall be designed to ensure reliable operation and to prevent false tripping.