| OGRR Number | 183 | OGRR Title | Administrative Changes for April 2006 Operating Guides |
| --- | --- | --- | --- |
| Status | Administrative Change |
| Operating Guide Section Requiring Revision | 2.4.3.1, Control Area Operations 4.4.18.1, Control Area Operations (PRR543 effective February 21, 2006) 4.5, Emergency Electric Curtailment Plan (EECP) 5.6.6.1, Emergency Electric Curtailment Plan (EECP) (PRR543) 5.6.7, EECP Steps (PRR543) |
| Revision Description | Administrative change to maintain Operating Guide consistency with Protocols as allowed by Operating Guide Section 1.3, Change Control Process. |
| Reason for Revision | PRR543 (Schedules and Emergency Assistance Over CFE-ERCOT DC Ties) has modified Protocol Sections that are referenced in the Operating Guides. This OGRR updates those references. |
| Timeline |
| Date Posted | 3/31/06 |
| Please access the ERCOT website for current timeline information. |

| Sponsor |
| --- |
| Name | Jeff Gilbertson, on behalf of OGRTF |
| E-mail Address | ogrevreq@ercot.com |
| Company | ERCOT |
| Company Address | 2705 West Lake Dr, Taylor, TX 76574 |
| Phone Number | 512-248-6462 |
| Fax Number |  |

ERCOT/Market Segment Impacts and Benefits

Instructions:  To allow for comprehensive PRR consideration, please fill out each block below completely, even if your response is “none,” “not known,” or “not applicable.”  Wherever possible, please include reasons, explanations, and cost/benefit analyses pertaining to the PRR.

| Assumptions | 1 | None |
| --- | --- | --- |
|  | Impact Area | Monetary Impact |
| Market Cost | 1 | None | None |
|  | Impact Area | Monetary Impact |
| Market Benefit | 1 | None | None |
| Additional Qualitative Information | 1 | Corrects out dated references in the Operating Guides. |
| Other | 1 |  |
| Comments | 2 |  |

Proposed Operating Guide Language Revision

#### 2.4.3.1	Control Area Operations

Reference:  Protocols Section 4.4.18.1, Control Area Operations

Control Area schedules between the ERCOT Control Area and interconnected non-ERCOT Control Area(s), through the use of schedules over Direct Current Tie(s), will be implemented in accordance with these Protocols, North American Electric Reliability Council (NERC) scheduling protocols, and in compliance with NERC operating policies.  Scheduling must also be in accordance with any applicable Federal Energy Regulatory Commission tariffs.

ERCOT will perform schedule confirmation with the applicable interconnected non-ERCOT Control Area(s) and, if appropriate, will coordinate the approval process for the NERC tags as both the ERCOT Control Area and on behalf of ERCOT TSPs.

## 4.5	Emergency Electric Curtailment Plan (EECP)

Reference:  Protocols Section 5.6.6.1, Emergency Electric Curtailment Plan (EECP) and Section 5.6.7, EECP STEPS

5.6.6.1	Emergency Electric Curtailment Plan (EECP)

At times it may be necessary to reduce electrical demand because of a temporary decrease in available electricity supply.  To provide orderly, predetermined procedures for curtailing demand during such emergencies, ERCOT will initiate and coordinate the implementation of the Emergency Electric Curtailment Plan following the EECP Steps set forth below in subsection 5.6.7.1, Restoration of Market Operations.

The objective of the EECP is to provide for maximum possible continuity of service while maintaining the integrity of the ERCOT Transmission Grid in order to reduce the chance of cascading outages.

ERCOT’s operating procedures shall meet the following goals while continuing to respect the confidentiality of market sensitive data:

(1)	Use of the market to the fullest extent practicable without jeopardizing the reliability of the ERCOT system;

(2)	Use of Responsive Reserve Services and other Ancillary Services to the extent permitted by ERCOT System conditions;

(3)	Maximum use of ERCOT System capability;

(4)	Maintenance of station service for nuclear Generation Resource Facilities;

(5)	Securing of startup power for Generation Resources;

(6)	Operation of power Generation Resources during loss of communication with ERCOT;

(7)	Restoration of service to critical Loads in the manner defined in the Operating Guides; and

(8)	Restoration of service to all customers following major system disturbances, giving priority to the larger groups of customers.

ERCOT shall be responsible for coordinating with QSEs and TDSPs to monitor system conditions, initiating the EECP steps set forth in this Section, notifying all QSEs, and coordinating the implementation of the EECP Steps while maintaining transmission security limits.

During the EECP, ERCOT has the authority to obtain energy from BtB Ties or Block Load Transfers (BLTs) from non-ERCOT Control Areas when capacity is available.

Some of the EECP Steps will not be applicable if transmission security violations exist. There may be insufficient time to implement all Steps in sequence, but to the extent practicable, ERCOT will use Ancillary Services which bidders have made available in the market to maintain or restore reliability.

ERCOT may immediately implement Step 4 of the EECP any time the steady-state system frequency is below 59.8 Hz and will immediately implement Step 4 any time the steady-state frequency is below 59.5 Hz.

Percentages for Step 4 Load shedding will be based on previous year’s TDSP peak Loads, as reported to ERCOT, and will be reviewed by ERCOT and modified annually.

5.6.7	EECP STEPS

Step 1 — Maintain 2300 MW of ERCOT’s Ancillary Service Resources comprised of: (1) undeployed Responsive Reserve Service; and (2) that amount of Non-Spinning Reserve Service which has been deployed but has not ramped to its specified output level.  ERCOT will:

(1)	Use those available Ancillary Services that can be deployed to increase Responsive Reserves.

(2)	Provide Dispatch Instructions to QSEs to start all Resources that are available in the time frame of the emergency (OOMC).  Similarly, ERCOT will provide Dispatch Instructions to QSEs to suspend any ongoing Generation Resource performance testing and maximize Resource deployment (OOME) to increase Responsive Reserve levels on other Resources.  QSEs intending to provide OOMC and OOME will comply as soon as practicable

(3)	Use available BtB import capacity that is not already being used and inquire about availability of Block Load Transfers.

(4)	Start RMR Units available in the time frame of the Emergency.  RMR Units should be loaded to full capability.

Step 2 — Maintain ERCOT undeployed Responsive Reserve Service on Generation Resources  equal to the largest Generation Resource on-line in ERCOT.  In addition to measures associated with Step 1, ERCOT will:

- Instruct TDSPs to reduce Load by using distribution voltage reduction management tools, if deemed beneficial by the TDSP.

- Deploy all Responsive Reserve, which is supplied from Load acting as a Resource (controlled by high-set under-frequency relays) to remove such Load.

- With the approval of the affected Non-ERCOT control area, may instruct TDSPs to implement BLTs, which transfer load from the ERCOT control area to Non-ERCOT control areas. Use of a BLT will be defined in the ERCOT operating Guides.

Step 3 – Maintain system frequency at 60 Hz

In addition to measures listed above, ERCOT will issue an appeal through the public media for voluntary Load curtailment.

Step 4 — Maintain system frequency at 59.8 Hz or greater

In addition to measures listed above, ERCOT will instruct, in 100 MW blocks, all TDSPs having control over distribution feeder breakers and/or control of breakers serving retail customers to shed Load in order to maintain a steady state system frequency of 59.8 Hz. ERCOT will allocate manual Load shedding for ERCOT-wide emergencies based on the amount of Load that is served by each TDSP.

5.6.7.1	Restoration of Market Operations

ERCOT shall continue EECP until sufficient bids are received and deployed by ERCOT to eliminate the conditions requiring the EECP.