## ERCOT Operations Report

## ROS & OWG

## January 2006

Frequency control   59.9 > F > 60.1

| Time | Frequency | Load | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
|  |  |  | (Max) | SCE | (Largest QSE Change) |
| 1/14/06 22:44 | 60.101 | 27357 | -536 | 431 | SCE |
| 1/20/06 9:19 | 59.880 | 30361 | -460 | -18 | AGC unintentionally changed from Constant Frequency Control to Tie Line Bias Control. |
| 1/23/06 6:03 | 59.899 | 32880 | 706 | -596 | 1850 (450) |
| 1/23/06 7:38 | 60.149 | 36204 | -1079 | -95 | Morning peak and drop off more pronounced than anticipated. 1000+ MW drop in ERCOT load 07:30 - 08:00. |
| 1/25/06 2:03 | 60.163 | 25855 | -412 | 82 | Operator calculated offset using generation data that was not updated for the correct interval. |

| Disturbance Data |  |  |
| --- | --- | --- |
| 1/7/06 21:30 | 59.854 | 500 MW |
| 1/12/06 12:13 | 59.784 | 600 MW |
| 1/12/06 12:25 | 59.882 | LaaR restoration |
| 1/16/06 6:47 | 59.826 | 765 MW |
| 1/25/06 4:43 | 59.870 | 530 MW |
| 1/29/06 13:41 | 59.852 | 520 MW |
| 1/30/06 0:35 | 59.774 | 735 MW |

Deployed Responsive (22) (Reported Above)

| 1/1/06 6:35 | 1/20/06 8:19 |
| --- | --- |
| 1/3/06 6:06 | 1/20/06 9:10 |
| 1/3/06 17:47 | 1/20/06 22:01 |
| 1/5/06 6:05 | 1/21/06 7:13 |
| 1/6/06 6:06 | 1/22/06 11:04 |
| 1/7/06 21:30 | 1/23/06 6:03 |
| 1/7/06 22:02 | 1/25/06 4:43 |
| 1/12/06 12:13 | 1/28/06 20:07 |
| 1/14/06 10:21 | 1/28/06 22:10 |
| 1/16/06 6:47 | 1/29/06 13:41 |
| 1/20/06 7:00 | 1/30/06 0:35 |

Day Ahead Capacity Purchases

| Historical OOMC/RMR | Jan 05 | Dec 05 | Jan 06 |
| --- | --- | --- | --- |
| DFW | 9 | 34 | 8 |
| E RIO | 9 | 83 | 48 |
| W RIO | 60 | 63 | 24 |
| Laredo | 44 | 40 | 40 |
| Bryan Area | 10 | 18 | 1 |
| Corpus | 31 | 9 | 9 |
| North | 0 | 4 | 6 |
| San Antonio | 0 | 24 | 34 |
|  | 167 | 299 | 170 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overload | Days |
| --- | --- | --- |
| Skyline - Marion - STP 345kV | Shertz - Parkway 138kV. | 9 |
| Bowie TMPP - Patterson St. 138kV | Bowie 138/69kV Transfomer | 6 |
| Lon Hill - North Edinburg 345kV | Lon Hill - Stratton 138kV | 5 |
|  | Bluff Creek - Oak Creek | 5 |
| Sandow 345/138kV auto | Sandow - Salty 138kV | 3 |
| San Angelo - Menard 138kV | Ballinger - Paint Rock 69kV | 3 |
| Dilley Sw - North Larado 138kV | Asherton - North Larado 138kV | 2 |
| La Palma - Rio Hondo 345kV | La Palma - Rio Hondo 138kV | 2 |
| Odessa EHV 345/138kV auto | Rexene Nylon Tap - Odessa EHV | 2 |
| STP - Skyline & Hill Country 345kV | Blessing - Lolita 138kV | 2 |
| Temple Switch - Bell County Switch 138kV | Poage - Temple Taylor Valley 69kV | 2 |
| Paris Switch - Valley SES 345kV | Allen Switch 345/138kV auto #2 | 2 |
| South - North |  | 2 |
|  | Sweetwater Tr | 2 |
| Batesville - Pearsall 138kV | Moore - Downie 138kV | 1 |
| Comanche Peak Units | Uvalde - Asphalt Mines 138kV | 1 |
| Comanche Peak Units | San Marcos - Canyon LCRA 138kV | 1 |
| Hill Country - Marion and STP 345kV | Schertz - Parkway 138kV | 1 |
| Jack County - Hill Top 138kV | Bowie 138/69kV autotransformer | 1 |
| Marion - Zorn & Clear Springs 345kV | Seguin - Zorn 138kV | 1 |
| Morgan Creek - Ector 345kV | General Tire Sw - Olefin Sw 138kV | 1 |
| Sonora - Friend Ranch 138kV | Friend Ranch - Ozona 69kV | 1 |
| Steephollow - Gibbons Creek 138kV | Perry 138/69kV auto | 1 |
| Steephollow - Gibbons Creek 138kV | Robertson - Watson Chapel 138kV | 1 |
| Gibbons Creek - Bryan East & Greens Prairie | Hearne - Hearne SW 69kV | 1 |
| Twin Oak - Gibbons Creek 345kV | Jewett - Watson Chapel 138kV | 1 |
| South - Houston |  | 1 |

New RAP

- None

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 01/17/2006 | Operating Period Desk - Emergency Site Failover | POB 235 |
| 01/17/2006 | Transmission & Security Desk - Emergency Site Failover | POB 234 |
| 01/16/2006 | Transmission & Security Desk - VSAT Procedure | POB 232 |
| 01/13/2006 | Frequency Control Desk - Maintenance Level 2 and 3 Outages | POB 231 |
| 01/17/2006 | Frequency Control Desk - Emergency Site Failover | POB 233 |

Blackout/Load Shed incidences

None

Major system voltage problems

None

Voltage Instructions

1/25	15:00	Lower instruction in North Zone

1/31	06:55	Lower instruction in South Zone

Corpus Christi RMR status summary

A major component of the Corpus area upgrade is expected to be in service during March.  ERCOT is developing a TSAT study to confirm the improvement in area stability.  The case preparation is expected to be completed by the time that the new components are in the Operations Model, and the decision to terminate RMR agreements will be made.

ERCOT has announced a need for a unit at Barney Davis for 2006.  Study results related to this decision are posted at the ERCOT Operations and System Planning data website under “Reliability Must-Run (RMR) Studies” folder ERCOTSempraRMRStudyFiles11152005.zip.

Major Computer Problems, Enhancements & Fixes

Voltage Stability tool for real time implemented in production.

1/4	10:30	Release 4 patches installed.

1/5	18:00	OOMC patch installed.

1/20	Control problems due to ERCOT AGC unintentionally changed from Constant Frequency Control to Tie Line Bias Control.

Communication

1/6	Held 00:00 interval due to an error detected in the Balancing calculation.

1/28	20:00	Conducted scheduled maintenance on Portal.

ERCOT peak (Unofficial)

1/18  	18:00	38,725

Alerts, OCN, and Emergency Notices

| 1-Jan | 12:10 | 13:00 | OCN | Capacity Insufficiency HE 19:00 - 20:00 |
| --- | --- | --- | --- | --- |
| 1-Jan | 13:00 | 23:00 | Alert | Capacity Insufficiency HE 19:00 - 20:00 |
| 8-Jan | 18:00 | 23:00 | OCN | Capacity Insufficiency HE 19:00 - 21:00 & 23:00 |
| 14-Jan | 2:40 | 6:30 | OCN | Capacity Insufficiency HE 08:00 - 09:00 |
| 14-Jan | 6:30 | 8:00 | OCN | Capacity Insufficiency HE 08:00 - 13:00 |
| 18-Jan | 2:15 | 4:15 | OCN | Capacity Insufficiency HE 08:00 |
| 31-Jan | 1:30 | 3:00 | OCN | Capacity Insufficiency HE 08:00 |
| 31-Jan | 3:00 | 7:00 | Alert | Capacity Insufficiency HE 08:00 |