## Slide 1
Motivation:
Response to NERC Recommendation 14
Purpose:
Assess the fidelity of the ERCOT dynamics models and data with actual system performance during the event.

## Slide 2
The Event:
August 19, 2004 Forney Plant Trip

## Slide 4
 | Requirements | DWG models and assumptions
Governor in service | Yes | Yes
Droop | 5 % | 5 %
Dead Band | ≤ ± .036 Hz | Not modeled
Reporting | Report if cannot supply governor response | Assume governors can supply response. A few are not modeled.
Governor Testing | Every 2 years | Data updated annually
Overall Response | 420 MW / .1 Hz | 404 MW / .1 Hz
Poor Governor Response | Lists elements leading to poor governor response. Says they should be avoided. | Models do not have the functions listed.

## Slide 9
 | Forney | CPSES
Time of Year | August 2004 | May 2003
Time of Day | 11:00 AM | 3:00 AM
Fault Involved? | No | Yes
Initial Generation Lost | 550 MW | 2300 MW
LaaR Shed? | Yes, limited | Yes
Firm Load Shed? | No | Yes
Initial Frequency Decline | 59.85 Hz | 59.3 Hz

## Slide 11
Include fault impedance
Increase governor droop
Change load model to include
some constant MVA

## Slide 12: DWG reached 20 conclusions. They are listed in the Conclusions section at the end of the report.

## Slide 13
Assess the fidelity of the ERCOT dynamics models and data
  Overall system inertia is OK
  Minor changes to load frequency model
  Tuning of some hydro governor models may be needed
  Governor Pmax values appear to be OK
  Current combined cycle models are inadequate
  The relay model used for LaaR is adequate
  Governor data appears to be consistent with ERCOT requirements, but does not adequately replicate actual system response