## ERCOT Operations Report

## ROS & OWG

## March 2006

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 3/3 3:00 | 60.106 | 22908 | -267 | 166 | ~150 MW drop in steel mill load during ramp period. |
| 3/4 12:04 | 60.105 | 28335 | -189 | 287 | ~150 MW drop in steel mill load during ramp period. |
| 3/4 19:59 | 60.105 | 30020 | 163 | -112 | ~270 MW drop in steel mill load during ramp period. |
| 3/13 18:01 | 60.103 | 31086 | 319 | 180 | Frequency < 60 Hz 17:42 - 17:55. ERCOT load decreased 300 MW across 18:00 ramp period. Evening peak ramped 18:30 -19:00 |
| 3/28 16:50 | 60.113 | 30091 | -89 | 135 | 150 MW Laar dropped & 140 MW steel mill load drop. |

| Disturbance Data |  |  |
| --- | --- | --- |
| 3/1 13:30 | 59.887 | 427 - 4 units |
| 3/8 6:16 | 59.867 | SMP failure documented in Communication section |
| 3/8 6:31 | 60.102 |  |
| 3/1 8:41 | 59.817 | 643 |
| 3/4 10:05 | 59.770 | 778 |
| 3/4 10:15 | 59.899 | Laar Reset |
| 3/9 0:42 | 59.825 | 540 |
| 3/9 0:54 | 59.845 | 265 |
| 3/9 1:48 | 60.136 | 2 VDI to raise generation 540 MW total 01:15 to 01:45 |
| 3/9 1:52 | 60.110 |  |
| 3/11 1:36 | 59.822 | 540 |
| 3/12 0:02 | 59.817 | 570 |
| 3/13 1:44 | 59.823 | 580 |

Deployed Responsive (13) (Reported Above)

| 3/1 8:41 | 3/9 0:42 | 3/20 6:10 |
| --- | --- | --- |
| 3/1 13:30 | 3/11 1:36 | 3/21 6:08 |
| 3/4 10:05 | 3/12 0:02 | 3/28 6:08 |
| 3/8 6:07 | 3/13 1:44 |  |
| 3/8 22:05 | 3/16 22:02 |  |

Day Ahead Capacity Purchases

| Historical OOMC/RMR | Mar 05 | Feb 06 | Mar 06 |
| --- | --- | --- | --- |
| DFW | 0 | 19 | 1 |
| E RIO | 33 | 72 | 85 |
| W RIO | 30 | 75 | 75 |
| Laredo | 34 | 41 | 59 |
| Bryan Area | 1 | 24 | 30 |
| Corpus | 31 | 6 | 1 |
| North | 0 | 11 | 0 |
| San Antonio | 0 | 38 | 26 |
| Western | 0 | 18 | 0 |
| Austin | 0 | 3 | 0 |
|  | 129 | 307 | 297 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overload | Days |
| --- | --- | --- |
| Bowie TMPP - Patterson Street 138kv | Bowie 138/69 auto | 8 |
| San Angelo - Menard 138kv | Ballinger - Paint Rock 69kv | 8 |
| Marion - Zorn & Clear Springs 345kv | Seguin - Seguin West 138kv | 6 |
| Odessa EHV 345/138kv auto | Rexene Nylon Tap - Olefin Sw | 6 |
| Marion - Zorn & Clear Springs 345kv | Zorn - Seguin 138kv | 4 |
| Hill Country - Marion & STP 345kv | Schertz - Parkway 138kv | 4 |
| Jack County - Patterson Street 138kv | Muenster - Saint Jo138kv | 2 |
| Northeast-North |  | 2 |
| South - Houston |  | 2 |
| North - Houston |  | 2 |
| North Edinburg 345/138kv auto | Rio Hondo - MVEC Burns | 2 |
| Paris Sw to Valley Sw 345kv | Commerce to Commerce South | 2 |
| San Miguel to Marion 345kv | Leon Creek to Pleasanton 138kv | 2 |
| Sonora to Hamilton 138kv | Uvalde to Asphalt Mines 138kv | 2 |
| Marion - Hill Country & Skyline 345kv | Geronimo - Seguin 138kv | 2 |
| West to North |  | 1 |
| Alice to Kingsville 138kv | Falfurrias Auto 138/69kv | 1 |
| Greenville Steam 138/69kv auto | Greenville Steam 138/69kv auto | 1 |
| Jack County - Bowie TMPP 138kv | Weatherford - Flat Rock Tap 138kv | 1 |
| Lon Hill-North Edinburg 345 | Rio Hondo - MV Burns 138 KV | 1 |
| Marion - Hill Country - Skyline 345kv | Schertz - Parkway 138kv | 1 |
| Marion - Zorn & Clear Springs 345kv | McCarty Lane - Henne 138kv | 1 |
| Menard T1 138/69kv auto | Ballinger - Paint Rock 69kv | 1 |
| Midland East-Odessa EHV 345 | ODEHV auto | 1 |
| Parker Switch - Eagle Mountain & Parker Switch - Roanoke 345kv | Benbrook Switch 345/138kv auto | 1 |
| Sonora - Friend Ranch 138kv | Friend Ranch - Ozona 69kv | 1 |
| Sonora - Friend Ranch 138kv | Friend Ranch - Crockett Heights | 1 |
| Spring - Bowie 138kv | Bowie 138/69kv auto | 1 |
| Temple Switch - Killeen Switch/ Temple Switch to Sandow 345kv | Belton - Harker Heights S | 1 |
| Trinidad - Stryker & Mt. Enterprise 345kv | Athens North Switch - Athens Tap | 1 |
| Vernon - Lake Pauline 138kv | Vernon - Chillicothe Vern Tap | 1 |
| Lon Hill - North Edinburg 345kv | Lon Hill - Stratton 138kv | 1 |
| Marion - Hill Country & Skyline 345kv | Comfort - Raymond Barker 138kv | 1 |
| Morgan Creek SES - Odessa EHV 345kv | Big Spring Sw - Big Spring West | 1 |
| Parker Sw-Eagle Mt-Roanoke Sw 345 | Benbrook 345/138 KV auto | 1 |

New RAP

- None

- New Procedures/ Forms/Operations Bulletins

| 03/30/2006 | Transmission & Security Desk V3R67 | 251 |
| --- | --- | --- |
| 03/30/2006 | Shift Supervisor Procedure V3R23 | 250 |
| 03/23/2006 | Day Ahead Desk Operating Procedure | 249 |
| 03/15/2006 | Scheduling Emergency Power Across the South DC Tie | 247 |
| 03/15/2006 | VDI Guideline to Relieve QSEs from AS Obligations | 246 |
| 03/01/2006 | Transmission & Security Desk - Western Area Action Plan for Voltage Support | 245 |

Blackout/Load Shed incidences

None

Major system voltage problems

None

Voltage Instructions

3/6	14:00	Raise instruction in South Zone

3/10	00:30	Lower instruction in the West Zone

3/10	04:00	2 raise instructions in the North Zone

3/15	00:30	2 lower instructions in the North Zone

3/23	03:00	Lower instruction in the South Zone

3/26  	02:00	Lower instruction in the South Zone

3/29	01:00	Lower instruction in the South Zone

Corpus Christi RMR status summary

2/19	Notification of RMR contract termination sent.

Major Computer Problems, Enhancements & Fixes

None

Communication

3/8	05:30 – 09:00	SMP failure caused by memory problems.  Both SMP servers were re-started and control was restored intermittently from 06:40 to 07:24 as the SMP servers competed for control of the ISD link.  RRS was deployed during the intermittent control, and several QSE SCE included the RRS obligation.  The SCE error was corrected by 09:00.

ERCOT peak (Unofficial)

3/31 17:00	38,400

Alerts, OCN, and Emergency Notices

| 1-Mar | 13:30 | 16:00 | OCN | Insufficient Balancing Energy available hours 1600 through 2000 |
| --- | --- | --- | --- | --- |
| 8-Mar | 14:15 | 18:06 | Transmission Alert | Loss of Kingsville - Alice 138 kV loads Falfurius 138/69 kV tr. |
| 11-Mar | 14:30 | 19:00 | Transmission Alert | Loss of Big Foot 138/69 kV tr loads Dilley2 - Pearsall 69 kV & Dilley Switch 138/69kV tr |
| 18-Mar | 20:57 | 24:00 | Transmission Emergency | Notice for the Hamilton and Uvalde areas due to a forced outage on the Sonora - Cauthorn 138 kV circuit. |
| 20-Mar | 9:30 | 19:00 | Transmission Alert | Loss of Kingsville - Alice 138 kV loads Falfurius 138/69 kV tr. |
| 20-Mar | 14:31 | 19:00 | Transmission Alert | Loss of San Angelo - Menard 138 kV loads Ballinger - Paint Rock 69 kV. |
| 21st - 23rd | 0:15 | 24:00 | Transmission Alert | Loss of Big Three - Victoria Dupont Switch 138kV circuit will island with BP Chemical Vistron - Black Bayou - Big Three 138kV circuits. |
| 24th – 25th | 09:34 | 23:55 | Transmission Alert | Loss of Aspermont – Spur or Aspermont – Paint Creek loads underlying system beyond 1st contingency limits |
| 29-Mar | 18:10 | 24:00 | Transmission Alert | Loss of Menard 138/69 kV tr or San Angelo - Menard 138 kV line loads Ballinger - Paint Rock 69 kV. |

Other

ERCOT Bias will be adjusted on 5/1 at 10:00 a.m. from 489/.1 Hz to 538/.1 Hz.

3/25	02:10	Spur – Aspermont Forced outage.  Voltage dropped and UVLS removed 27.5 MW load, resulting in high voltage.  Additional lines and 16 MW of load manually opened due to the high voltage.  All load restored by 04:40 and the initial contingency was restored at 20:40.

3/18 -19 Thunderstorms in West Texas caused the loss of nine 69 kV lines and four 138 kV lines

3/28	13:00 – 14:10	Multiple lines in the Austin area tripped during thunderstorms.

3/30	Tradinghouse bus cleared, tripping Tradinghouse – Venus, Tradinghouse – Lake Creek, and Lake Creek – Jewett 345 kV lines.