## Slide 1: ERCOT Systems Operations Report
Draft PRR Update for Non-Spin Deployment Recall Practices
Report on Historical Frequency at 1800
Valley Area Overlimit Analysis
March 21st RRS Deployment

## Slide 2: 3/21 RRS Deployment
18 minute deployment of RRS shortly after 06:00 ramp period in response to frequency < 59.91 Hz.
  Up Regulation depleted at 06:05 due to
    a.m. load pickup
      ~1300 per interval
    +4120 schedule change
      Balanced down 3175 to counter

## Slide 3: 3/21 RRS Deployment

## Slide 6: 5/25/05 Reversals of Regulation = 448
 | August | October | December
minimum | 363 | 370 | 357
maximum | 926 | 1036 | 1102
average | 496 | 682 | 608
stddev | 132 | 129 | 176

## Slide 7
24-Jan | 7:35 | Planned Outage of Lon Hill - Rio Hondo
24-Jan | 14:13 | OOME
24-Jan | 14:52 | OOMC
24-Jan | 15:04 | VDI
24-Jan | 17:52 | OOME
24-Jan | 17:53 | OOME
24-Jan | 19:00 | TO reports valley import limit exceeded
25-Jan | 0:15 | oome_vdi
25-Jan | 0:15 | oome_vdi
25-Jan | 6:00 | OOMC
25-Jan | 7:35 | TO reports valley import limit exceeded
25-Jan | 15:00 | Problem ID'd - Contingency set to Full Processing.
25-Jan |  | Limit established through manual simulation of contingency.
25-Jan | 15:14 | VDI
25-Jan | 17:42 | OOME
25-Jan | 17:51 | OOME
25-Jan | 17:57 | OOME
25-Jan | 19:00 | OOMC
25-Jan | 22:11 | Restored Rio Hondo - Lon Hill outage
27-Jan |  | VSAT application for Valley import available
 |  | Screening tolerance lowered to .8. Contingency remains in Full Processing