## ERCOT Operations Report

## ROS & OWG

## February 2006

Frequency control   59.9 > F > 60.1

|  |  |  | Reg | ERCOT | Schedule Change |
| --- | --- | --- | --- | --- | --- |
| Time | Frequency | Load | (Max) | SCE | (Largest QSE Change) |
| 2/1/2006 22:03 | 59.896 | 29214 | -90 | -70 | -3675 (-1270) |
| 2/17/06 5:48 | 60.122 | 29521 | -368 | 534 | 985 (560) |
| 2/21/2006 5:10 | 59.827 | 31984 | 319 | -1185 | EMMS Stopped deploying regulation at 04:55 - 05:11 |
| 2/26/2006 18:37 | 59.898 | 29588 | 940 | -212 | 2750 MW load increase 18:15 - 19:00, Up Reg depleted 18:30 - 19:00. |

| Disturbance Data |  |  |
| --- | --- | --- |
| 2/9/2006 14:16 | 59.897 | 361 MW trip. |
| 2/11/2006 19:59 | 59.878 | 317 MW trip. |
| 2/17/2006 19:32 | 59.842 | 620 MW trip. |
| 2/27/2006 16:23 | 59.866 | 430 MW trip. |

Deployed Responsive (12) (Reported Above)

| 2/1/06 21:59 | 2/8/06 6:10 | 2/17/06 19:32 |
| --- | --- | --- |
| 2/2/06 9:45 | 2/8/06 8:02 | 2/21/06 5:02 |
| 2/5/06 11:05 | 2/9/06 14:16 | 2/26/06 18:37 |
| 2/7/06 6:07 | 2/11/06 19:59 | 2/27/06 16:23 |

Day Ahead Capacity Purchases

| Historical OOMC/RMR | Feb 05 | Jan 06 | Feb 06 |
| --- | --- | --- | --- |
| DFW | 8 | 8 | 19 |
| E RIO | 54 | 48 | 72 |
| W RIO | 29 | 24 | 75 |
| Laredo | 36 | 40 | 41 |
| Bryan Area | 13 | 1 | 24 |
| Corpus | 28 | 9 | 6 |
| North | 0 | 6 | 11 |
| San Antonio | 0 | 34 | 38 |
| Western | 1 | 0 | 18 |
| Austin | 0 | 0 | 3 |
|  | 180 | 170 | 307 |

OOME / Congestion Management Activity

Indicates congestion affected by outages

Indicates a Remedial action plan has been developed for the element

| Contingency | Overload | Days |
| --- | --- | --- |
| Bowie TMPP - Patterson Street 138 kV | Bowie 138/69 kV Tr | 17 |
| Comanche Peak 1 & 2 | Uvalde-Asphalt Mines | 17 |
| Lon Hill -N Edinburg 345 kV | Lon Hill - Stratton/Voltage violations | 13 |
| Skyline - Marion & STP 345 kV | Schertz - Parkway 138 kV | 11 |
| Hill Country - Marion & STP 345 kV | Schertz - Parkway 138 kV | 10 |
| Marion - Hill Country & Skyline 345 kV | Schertz - Parkway 138 kV | 8 |
| South - North |  | 5 |
| North Edinburg 345/138 kV Tr | Rio Hondo - MV Burns 138 kV | 4 |
| South - Houston |  | 3 |
|  | Buffalo Gap-Abilene South 138 kV | 3 |
| Austrop - Lost Pines 345 kV | Fayetteville 345/138 kV Tr #2 | 2 |
| Austrop - Sandow 345 kV | Austrop 345/138 kV Tr #2 | 2 |
| Odessa EHV Switch 345/138 kV Tr | Odessa EHV Switch - Olefin Switch 138 | 2 |
| North - West |  | 2 |
|  | Lon Hill - Stratton | 2 |
| Abilene South-Eskota Sw 138 kV | Eskota SW 138/69 kV Tr | 1 |
| Uvalde 138/69 kV Tr | Asherton 138/69 kV Tr | 1 |
| Austrop - Lost Pines 345 kV | Austrop 345/138 kV Tr | 1 |
| Fisher Rd-Oklaunion-Bowman 345 kV | Lake Pauline 138/69 kV Tr | 1 |
| Graham - Benbrook & Parker Sw 345 kV | Stephenville - Lingleville 138 kV | 1 |
| Kerrville Stadium-Comfort 138 kV | Comfort-Raymond Barker 138 kV | 1 |
| Lytton Springs to Zorn 345 kV | Canyon to San Marcos 138 kV | 1 |
| Morgan Creek 345/138 kV Tr | Morgan Creek 345/138 kV Tr #2 | 1 |
| Mt. Enterprise-Trinidad-Martin Lake 345 kV | Nacogdoches 345/138 kV Tr | 1 |
| Odessa EHV 345/138 kV Tr | Odessa EHV 345/138 kV Tr | 1 |
| Odessa EHV 345/138 kV Tr | Odessa EHV - Rexene Nylon Tap | 1 |
| Odessa EHV SW 345/138 kV Tr | REXEN Nylon Tap-Olefin Sw 138 kV Tr | 1 |
| Rio Hondo 345/138 kV Tr | Weslaco - Heidelburg 138 kV | 1 |
| San Angelo - Menard 138kV | Ballinger - Paint Rock 69 kV | 1 |
| Sandow - Temple Switch 345 kV Tr | Uvalde - Asphalt Mines 138 kV | 1 |
| Sweeny Cogen 138/69 kV Tr | Phillips-Phillips Petrol3 69 kV | 1 |
| Uvalde to Asherton 138kV | Uvalde 138/69 kV Tr | 1 |
| GBY – King 345 kV | GBY Tr 1 | 1 |
|  | Airport 138/69 kV Tr | 1 |

New RAP

- None

- New Procedures/ Forms/Operations Bulletins

| Date | Subject | Bulletin# |
| --- | --- | --- |
| 02/28/2006 | Transmission & Security Desk - Block Load Transfer | 244 |
| 02/28/2006 | Transfer Procedures to a New Location | 243 |
| 02/28/2006 | Frequency Control Desk - South DC Tie | 242 |
| 02/28/2006 | Frequency Control Desk - South DC Tie | 241 |
| 02/15/2006 | Operating Period Desk - NSRS Deployments | 239 |
| 02/15/2006 | Day Ahead Desk - Operating Procedure Manual | 238 |
| 02/15/2006 | Transmission and Security Desk - Conducting Security Analysis | 237 |

Blackout/Load Shed incidences

None

Major system voltage problems

None

Voltage Instructions

2/11	02:00	Lower instruction in South Zone

2/21	03:00	Lower instruction in South Zone

Corpus Christi RMR status summary

2/19	Notification of RMR contract termination sent.

Major Computer Problems, Enhancements & Fixes

2/8	PR40113 RAP-C Modeling Enhancements implemented

2/21	05:00 – 05:11	Out of memory error caused SMP to fail.  Regulation deployments were not being updated.  A patch installed on 3/13 is expected to fix the issue.

Communication

2/9	Held 09:30 interval.  MCP suspect.

2/21	Held 14:30 interval.  Erroneous value entered into OC1 constraint.

ERCOT peak (Unofficial)

2/18 20:00	43,370

Alerts, OCN, and Emergency Notices

| 4-Feb | 8:00 | 8:25 | OCN | Capacity shortage for Hour Ending 10:00 |
| --- | --- | --- | --- | --- |
| 4-Feb | 8:25 | 9:15 | Alert | Capacity shortage for Hour Ending 10:00 |
| 16-Feb | 17:15 | 20:15 | OCN | Insufficient UBES bids for operating hour 20:00. |
| 17-Feb | 11:00 | 24:00 | Advisory | Cold temperature and freezing precipitation forecasted through Sunday. |
| 18-Feb | 0:15 | 24:00 | Advisory | Cold temperature and freezing precipitation forecasted through Sunday. |
| 18-Feb | 15:00 | 22:30 | Alert | Loss of Live Oak-Sonora loads Conoco - Lake Nasworthy. |
| 18-Feb | 15:00 | 22:30 | Alert | Loss of Asherton 138/69 kV Tr loads Uvalde 138/69 kV Tr |
| 18-Feb | 15:00 | 16:45 | Alert | Loss of Menard 138/69 kV Tr loads Ft Mason - Mason TO. |
| 19-Feb | 0:15 | 24:00 | Advisory | Cold temperature and freezing precipitation forecasted through Sunday. |
| 19-Feb | 4:45 | 13:45 | Alert | Loss of Kingsville - Alice loads Falfurrias 138/69 kV Tr |
| 19-Feb | 10:45 | 22:00 | Alert | Loss of Live Oak-Sonora loads Conoco - Lake Nasworthy. |
| 19-Feb | 10:45 | 22:00 | Alert | Loss of Asherton 138/69 kV Tr loads Uvalde 138/69 kV Tr |
| 19-Feb | 10:45 | 22:00 | Alert | Loss of Big Foot 138/69 kV Tr loads Dilley - Pearsall and loss of Dilley Switch- San Miguel loads Derby to Pearsall |
| 20-Feb | 0:15 | 14:00 | Advisory | Cold temperature and freezing precipitation forecasted through Monday 2-20 |
| 20-Feb | 3:30 | 7:30 | OCN | Capacity shortage for Hour Ending 8:00 |
| 21-Feb | 5:15 | 5:30 | Emergency Notice | EMMS Regulation, Responsive Deployments are not being sent. |
| 27-Feb | 10:45 | 12:30 | Alert | Loss of Orange Grove- Lon Hill loads Three Rivers 138/69 kV Tr |
| 27-Feb | 10:45 | 12:30 | Alert | Loss of George West - Sigmor or George West 138/69 kV Tr cause voltage violations on the 69kv system |
| 28-Feb | 12:50 | 14:30 | OCN | Capacity shortage for Hour Ending 20:00 |

Other

1/25	RTCA failed to identify a system operating limit violation in the Rio Grande Valley.  Even though the screening processes identified the contingency was above the threshold to push it to full processing, it was labeled as ‘harmless’ and was not processed.  A new process has been developed to build a daily list of contingencies that will be set to full processing regardless of the screening results.