## Slide 1
April 17, 2006 EECP Event

## Slide 2: Sequence of Events
Going into April 17
  Peak load forecast – 49,018 MW
  Peak capacity scheduled – 53,920 MW
  Capacity on planned outage – 14,000 MW
Hour ending 3:00 pm demand was 50,265 MW
At 3:25 pm EECP Step 1 was declared
  All balancing bids and regulation being used
  Spinning reserve deployed
  Difficulty maintaining 60 Hz
  Asked for all capacity available to be brought on line and generating
  Scheduled emergency assistance over the DC ties
*all numbers are preliminary

## Slide 3: Sequence of Events (cont.)
At 3:34 pm EECP Step 2 declared
  Continued low frequency with all balancing and regulation deployed
  Deployed all LaaRs (interruptible loads providing Responsive Reserve – 1,150 MW)
  Frequency recovered to 60 Hz
Hour ending 4:00 pm load was 51,714 MW
Shortly after 4:00 pm several units tripped within a few minutes of each other ~1,200 MW total
  Frequency went below 59.8 HZ
*all numbers are preliminary

## Slide 4: Sequence of Events (cont.)
At 4:13 pm EECP Step 4 declared
  Ordered 1,000 MW firm load shedding
  Allocated to Transmission Operators on a load ratio share basis
  Rotated among customers
At 4:25 pm Step 3 of the EECP (Public Appeal for Conservation) was issued
  Frequency recovered but balancing and regulation continued to be fully used until about 5:30 pm
At 5:31 pm ERCOT started reducing firm load curtailments
*all numbers are preliminary

## Slide 5: Sequence of Events (cont.)
At 6:10 pm all firm load restored
At 6:21 pm started restoring LaaRs (interruptible) load)
EECP fully cancelled at 7:20 pm
*all numbers are preliminary

## Slide 6: April 18 Preparation
Planning for a peak load of 53,575 MW
Expecting 58,100 MW of generation to be available scheduled by QSEs and procured by ERCOT
*all numbers are preliminary