ERCOT Protocols

Section 6:  Ancillary Services

March 1, 2006

6	Ancillary Services	6-1

6.1	Ancillary Services Required by ERCOT	6-1

6.2	Providers of Ancillary Services	6-5

6.3	Responsibilities of ERCOT and Qualified Scheduling Entities	6-5

6.4	Standards and Determination of the Control Area Requirements for Ancillary Services	6-8

6.5	Technical Requirements for Providers of Ancillary Services	6-10

6.6	Selection Methodology	6-40

6.7	Deployment Policy	6-47

6.8	Compensation for Services Provided	6-59

6.9	Settlement for ERCOT-Provided Ancillary Services	6-120

6.10	Ancillary Service Qualification, Testing and Performance Standards	6-137

# Ancillary Services

6.1	Ancillary Services Required by ERCOT

ERCOT shall be responsible for developing a daily Ancillary Services Plan with sufficient Ancillary Services (AS) to maintain the security and reliability of the ERCOT System consistent with ERCOT and North American Electric Reliability Council (NERC) standards.  The Ancillary Services required by ERCOT are described below.  ERCOT shall procure and deploy Ancillary Services on behalf of QSEs.

6.1.1	Balancing Energy Service

As provided by ERCOT to the Qualified Scheduling Entities (QSEs): Balancing Energy is deployed by ERCOT with the goals that (1) Regulation Service in either direction not be depleted during the interval, and (2) Regulation Service up and down energy is deployed in each Settlement Interval such that the net energy in regulation is minimized.

As provided by a QSE to ERCOT: The provision of incremental or decremental energy dispatched by Settlement Interval to meet the balancing needs of the ERCOT System.

6.1.2	Regulation Service – Down

As provided by ERCOT to the QSEs: Regulation-down power is deployed in response to an increase in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.

As provided by a QSE to ERCOT: The provision of Generation Resource capacity to ERCOT so that ERCOT can deploy power for the purpose of controlling frequency by continuously balancing generation and Load within the ERCOT System.

[PRR307: Revise Section 6.1.2 as follows when system change implemented.] As provided by a QSE to ERCOT: The provision of Resource capacity to ERCOT so that ERCOT can deploy power for the purpose of controlling frequency by continuously balancing generation and Load within the ERCOT System.

6.1.3	Regulation Service-Up

As provided by ERCOT to the QSEs: Regulation up power is deployed in response to a decrease in ERCOT System frequency to maintain the target ERCOT System frequency within predetermined limits according to the Operating Guides.

As provided by a QSE to ERCOT: The provision of Generation Resource capacity to ERCOT so that ERCOT can deploy power for the purpose of controlling frequency by continuously balancing generation and Load within the ERCOT System.

[PRR307: Revise Section 6.1.3 as follows when system change implemented.] As provided by a QSE to ERCOT: The provision of Resource capacity to ERCOT so that ERCOT can deploy power for the purpose of controlling frequency by continuously balancing generation and Load within the ERCOT System.

6.1.4	Responsive Reserve Service

As provided by ERCOT to the QSEs: Operating reserves ERCOT maintains to restore the frequency of the ERCOT System within the first few minutes of an event that causes a significant deviation from the standard frequency.  Furthermore, Responsive Reserve Service provides reserved Resources that are deployed for the Operating Hour in compliance with these Protocols in response to loss-of-Resource contingencies on the ERCOT System.

As provided by a QSE to ERCOT: The provision of capacity by unloaded Generation Resources that are on line, Resources controlled by high set under-frequency relays or from Direct Current (DC) tie response.  The amount of capacity from unloaded Generation Resources or DC Tie response is limited to the amount allowed in the Operating Guides or that, which can be deployed within 15 seconds.

[PRR307: Revise Section 6.1.4 as follows when system change implemented.] As provided by a QSE to ERCOT: The provision of capacity by unloaded Generation Resources that are on line, Load Resources capable of controllably reducing or increasing consumption under dispatch control (similar to AGC) and that immediately responding proportionally to frequency changes (similar to generator governor action), and Resources controlled by high set under-frequency relays or from Direct Current (DC) Tie response. The amount of capacity from unloaded Generation Resources or DC Tie response is limited to the amount allowed in the Operating Guides or that, which can be deployed within 15-seconds.

6.1.5	Non-Spinning Reserve Service

As provided by ERCOT to the QSEs: Reserves maintained by ERCOT, that are deployed for the Operating Hour in response to loss-of-Resource contingencies on the ERCOT System.

As provided by a QSE to ERCOT: Off-line Generation Resource capacity, or reserved capacity from On-line Generation Resources, capable of being ramped to a specified output level within thirty (30) minutes or Loads acting as a Resource that are capable of being interrupted within thirty (30) minutes and that are capable of running (or being interrupted) at a specified output level for at least one (1) hour.

6.1.6	Replacement Reserve Service

As provided by ERCOT to the QSEs: The instruction, by ERCOT, for the deployment of Loads or non-synchronized Generation Resources in order to make available additional Balancing Energy Service.

As provided by a QSE to ERCOT: A Resource capable of providing additional Balancing Energy Service to ERCOT when deployed.

6.1.7	Voltage Support

As provided by ERCOT to the QSEs and the TDSPs: The coordinated scheduling of Voltage Profiles at transmission busses to maintain transmission voltages on the ERCOT System in accordance with Operating Guides.

As provided by a QSE to ERCOT: The provision of capacity from a Generation Resource required to provide VSS, whose power factor and output voltage level can be scheduled by ERCOT to maintain transmission voltages within acceptable limits throughout the ERCOT System in accordance with Operating Guides.

6.1.8	Black Start Service

As provided by ERCOT to QSEs: The procurement by ERCOT through Agreements, pursuant to emergency Dispatch by ERCOT and emergency restoration plans of Resources which are capable of self-starting or Resources within close proximity of another power pool which are capable of starting from such power pool via a firm standby power supply contract, without support from the ERCOT System, or transmission equipment in the ERCOT System in the event of a blackout, in order to begin restoration of the ERCOT System to a secure operating state.  Resources which can be started with a minimum of pre-coordinated switching operations using ERCOT transmission equipment within the ERCOT System may be considered for Black Start Service only where switching may be accomplished within one (1) hour or less.

As provided by a Generator or a QSE to ERCOT: The provision of Resources under a Black Start Agreement, pursuant to emergency Dispatch, which are capable of self-starting or Resources within close proximity of another power pool which are capable of starting from such power pool via a firm standby power supply contract, without support from the ERCOT System, or transmission equipment in the ERCOT System in the event of a blackout.  Resources which can be started with a minimum of pre-coordinated switching operations using ERCOT transmission equipment within the ERCOT System may be considered for Black Start Service only where switching may be accomplished within one (1) hour or less.

6.1.9	Reliability Must-Run Service

As provided by ERCOT to QSEs: Agreements for capacity and energy from Resources which otherwise would not operate and which are necessary to provide voltage support, stability or management of localized transmission constraints under first contingency criteria, as described in the Operating Guides, where Market Solutions do not exist.  This includes service provided by RMR Units and MRA Resources.

As provided by a QSE to ERCOT: The provision of Generation Resource capacity and/or energy Resources under a Reliability Must-Run (RMR) Agreement or a Must Run Alternative (MRA) Agreement, including Agreements with Synchronous Condenser Units, whose operation is directed by ERCOT.

6.1.10	Out of Merit Capacity Service

As provided by ERCOT to QSEs:  The provision by ERCOT of Out of Merit Order (OOM) Replacement Reserve Service from Generation Resources, that would otherwise not be selected to operate because of their place (or absence) in the Merit Order of Resources’ bids for Ancillary Services.  OOMC is used by ERCOT to provide for the availability of sufficient capacity so that Balancing Energy bids are available to solve capacity insufficiency, Congestion, or other reliability needs, when a Market Solution does not exist. Loads Acting as Resources will not be available to ERCOT to provide OOMC Service.

As provided by a QSE to ERCOT:  Generation capable of providing additional Balancing Energy Service to ERCOT when deployed.

6.1.11	Out-Of-Merit Energy Service

As provided by ERCOT to QSEs: The deployment by ERCOT for the Settlement Interval of energy from Resources, that may or may not have provided Resource-specific premium bids, and used by ERCOT to provide Balancing Energy Service when no Market Solution exists for resolving Congestion, the actuation for specific units under an ERCOT approved Special Protection System, or, if required, in declared emergencies as described in these Protocols.

As provided by a QSE to ERCOT: The provision of incremental or decremental energy dispatched from a specific Resource in emergency operations by Settlement Interval in Real Time to meet the balancing needs of the ERCOT System when no Market Solution exists or in declared emergencies.

6.1.12	Zonal Out-of-Merit Energy (Zonal OOME) Service

As provided by ERCOT to QSEs: The deployment by ERCOT for the Settlement Interval of energy from a QSE's fleet of Resources, that may or may not have provided Resource-specific premium bids, and used by ERCOT when all other methods for resolving Congestion have failed or if required in declared emergencies as described in these Protocols.

As provided by a QSE to ERCOT: The provision of incremental or decremental energy Dispatched from a QSE's fleet of Resources in emergency operations by Settlement Interval in Real Time to meet the needs of the ERCOT System when all other methods for resolving Congestion have failed or in declared emergencies.

6.2	Providers of Ancillary Services

6.2.1	Ancillary Services Provided Solely by ERCOT

ERCOT is the sole provider of system-wide Balancing Energy Service; Generation Resource unit-specific Voltage Support Service (VSS), Black Start Service, Replacement Reserve Service, Zonal OOME Service, RMR Service, OOMC, and OOME Service to QSEs.

ERCOT will arrange Resources to provide system-wide VSS, Black Start, Zonal OOME, and RMR Service from QSEs.  ERCOT will direct Resources to provide OOMC or OOME in accordance with OOMC Service and OOME Service provisions of these Protocols.

6.2.2	Ancillary Services Provided in Part by ERCOT and in Part by Qualified Scheduling Entities

Each QSE may self-arrange its Obligation assigned by ERCOT for each of the following Ancillary Services:  Regulation Up, Regulation Down, Responsive Reserve, and Non-Spinning Reserve.  Any of the Ancillary Services that are not self-arranged will be procured as a service by ERCOT on behalf of the QSEs.

6.3	Responsibilities of ERCOT and Qualified Scheduling Entities

6.3.1	ERCOT Responsibilities

(1)	ERCOT, through its Ancillary Services function, shall develop the Operating Day Ancillary Services Plan for the ERCOT System, and the Day Ahead Ancillary Service Obligation which will be assigned based on Load Ratio Share data, by LSE, aggregated to the QSE level.  Unless otherwise provided in these Protocols, a QSE’s allocation for Ancillary Service Obligation will be determined for each hour according to that LSE’s Load Ratio Share computed by ERCOT.  The LSE Ancillary Service allocation for the Day Ahead Ancillary Service Obligation shall be based on the hourly Load Ratio Share from the Initial Settlement data, for the Operating Day that is twenty-one (21) days before the day in which the Obligation is being calculated, as defined in Section 9.2, Settlement Statements, for the same hour and day of the week multiplied by the quantity of the service in the Operating Day Ancillary Service Plan.

[PRR426: Replace Section 6.3.1, item (1) above with the following upon system implementation:] (1) ERCOT, through its Ancillary Services function, shall develop the Operating Day Ancillary Service Plan for the ERCOT System., The Day Ahead Ancillary Service Obligation, except for Regulation Service, will be assigned based on Load Ratio Share data, by LSE, aggregated to the QSE level. The Day Ahead Regulation Service Obligation will be assigned based on Energy Ratio Share data, by LSE and Generation Resource, aggregated to the QSE level. Unless otherwise provided in these Protocols, a QSE’s allocation for all Ancillary Service Obligations except Regulation Service will be determined for each hour according to that LSE’s Load Ratio Share computation by ERCOT. For all Ancillary Services Obligations except Regulation Service, the LSE Ancillary Service allocation for the Day Ahead Ancillary Service Obligation shall be based on the hourly Load Ratio Share from the Initial Settlement data, for the Operating day that is twenty-one (21) days before the day in which the Obligation is being calculated, as defined in Section 9.2, Settlement Statements, for the same hour and day of the week multiplied by the quantity of the service in the Operating Day AS Plan. For Regulation Service, the LSE plus the Generation Resource Ancillary Service allocation shall be the hourly Energy Ratio Share of the Load data and the data from Uncontrollable Renewable Resources electing to utilize Renewable Production Potential for URC and OOME from the Initial Statement, as defined in Section 9.2, Settlement Statements, for the same hour and day of the week multiplied by the quantity of the service in the Operating Day Ancillary Service Plan.

[PRR568: Replace "twenty-one (21)" with "fourteen (14)" in paragraph (1) above (boxed and unboxed) upon completion of the transition plan.]

(2)	ERCOT shall procure required Ancillary Services not self-arranged by QSEs.

(3)	ERCOT accepts Ancillary Service bids only from QSEs.

(4)	ERCOT shall allow the same capacity to be bid as multiple Ancillary Services types recognizing that this capacity may only be selected for one service.

(5)	ERCOT shall ensure provision of Ancillary Services to all ERCOT System Market Participants in accordance with these Protocols.

(6)	ERCOT shall not discriminate when obtaining Ancillary Services from QSEs submitting Ancillary Service bids.  ERCOT shall not discriminate between Self-Arranged Ancillary Services and ERCOT-procured Ancillary Services when dispatching Ancillary Services.

(7)	For AS that are not self-arranged, ERCOT shall procure any additional Resources ERCOT requires during the Day-Ahead Scheduling Process, the Adjustment Period process, or the Operating Period.

(8)	ERCOT shall procure Resources that are used to provide Reliability Must-Run Service or Black Start Service through longer-term Agreements.

(9)	Following submission of QSE self-arranged schedules, ERCOT will identify the remaining amount of Ancillary Services that must be acquired in order to complete ERCOT’s Day-Ahead Ancillary Services Plan.  Regulation Up, Regulation Down, Responsive, and Non-Spinning services will be procured by ERCOT on the timeline described in Section 4, Scheduling.

(10)	ERCOT will not profit financially from the market.  ERCOT will follow the Protocols with respect to the procurement of Ancillary Services and will not otherwise take actions regarding Ancillary Services with the intent to influence, set or control market prices.

(11)	ERCOT will provide that Market Clearing Prices are posted on the Market Information System (MIS) in a timely manner as stated in Section 12.4.1, Scheduling Information, of these Protocols.  ERCOT will monitor Market Clearing Prices for errors and will “flag” for further review questionable prices before posting, and make adjustments or notations in the posting if there are conditions that cause the price to be questionable.  ERCOT may only correct the price consistent with these Protocols.

(12)	ERCOT shall post the aggregated ERCOT AS Bid Stacks in accordance with Section 12.4.2, Ancillary Service Related Information of these Protocols.

(13)	ERCOT will, through procurement processes specified in these Protocols, procure Ancillary Services as required and charge QSEs for those Ancillary Services in accordance with these Protocols.

(14)	ERCOT will ensure ERCOT electric network reliability and adequacy and will afford the market a reasonable opportunity to supply reliability solutions.

(15)	ERCOT will not substitute one type of Ancillary Service for another.

(17)	ERCOT shall make reasonable efforts to minimize the use of OOMC, Zonal OOME, or contracted RMR Facilities.  This includes entering into MRA Agreements with Resources selected through the planning process, pursuant to Section 6.5.9.2, to provide services to meet reliability requirements at lower total expected costs than would otherwise be provided by RMR Agreements.

(18)	ERCOT will provide timely information to those Resource units providing OOMC and RMR Services as to the specific use of each unit dispatched.

6.3.2	Qualified Scheduling Entity Responsibilities

(1)	Unless contracted otherwise, and with the exception of Balancing Energy decremental bids as described in Section 4, Scheduling, of these Protocols, Resources capable of providing Ancillary Services are not required to provide those Resources or to submit bids to ERCOT, provided, however, Resources shall honor bids submitted to ERCOT for Ancillary Services under these Protocols and shall, use reasonable efforts to provide Ancillary Services in accordance with applicable emergency procedures in these Protocols and in the Operating Guides.

(2)	Ancillary Service providers shall provide and deploy, as directed by ERCOT, the Ancillary Service(s) that they have agreed to provide.

(3)	QSEs may specify Self-Arranged Ancillary Services in accordance with the Day-Ahead Scheduling as described in Section 4.4, Day Ahead Scheduling Process.

[PIP106: Current design does not provide for DLC Profiles. When DLC Profiles are implemented add this item (4) to section 6.3.2] (4) QSEs that have Direct Load Control programs as described in Section 18.7.2, Load Profiling of ESI IDs Under Direct Load Control, will notify ERCOT immediately of any deployment of the program. This applies solely to QSEs using Load Profiling for Settlement.

6.4	Standards and Determination of the Control Area Requirements for Ancillary Services

6.4.1	Standards for Determining Ancillary Services Quantities

(1)	ERCOT shall comply with the requirements for determination of Ancillary Service quantities as specified in these Protocols and the Operating Guides.

(2)	ERCOT shall, at least annually, determine with supporting data, the methodology for determining the minimum quantity requirements for each Ancillary Service needed for reliability, including the percentage of Load acting as a Resource allowed to provide Responsive Reserve Service calculated on a monthly basis.

(3)	ERCOT shall initially determine the percentage of Load acting as a Resource on a calendar month basis for the remainder of the current year allowed to provide Responsive Reserve Service within ninety (90) days after implementation of this Protocol revision.

(4)	The ERCOT Board shall review and approve ERCOT's methodology for determining the minimum Ancillary Service requirements and the monthly percentage of Load acting as a Resource allowed to provide Responsive Reserve Service.

(5)	If ERCOT determines a need for additional Ancillary Service Resources pursuant to these Protocols or the Operating Guides, after an Ancillary Services Plan for a specified day has been posted, ERCOT will inform the market by posting on the Market Information System, of ERCOT’s intent to procure additional Ancillary Service Resources in accordance with Section 4.5.8, ERCOT Notice to Procure Additional Ancillary Services.  ERCOT will post the reliability reason for the increase in service requirements.

(6)	Once specified by ERCOT for an hourly interval, Ancillary Service quantity requirements may not be decreased.

(7)	ERCOT shall instruct such that sufficient Resource capacity is on line, in appropriate locations, and available to ERCOT to meet the potential needs of the ERCOT System.

(8)	ERCOT shall include in its AS plan sufficient capacity to automatically control frequency to meet NERC standards.

(9)	ERCOT will post Engineering Studies on the MIS representing specific Ancillary Service requirements as described in Section 12, ERCOT Market Information System.

6.4.2	Determination of ERCOT Control Area Requirements

By the twentieth (20th) day of the current month, ERCOT will post a forecast of minimum Ancillary Services quantity requirements for the next calendar month.

Prior to 0600 of the Day Ahead, ERCOT will use the Day Ahead Load forecast and will develop an Ancillary Services Plan that identifies the amount of Ancillary Services necessary for each hour of the next day as specified in Section 4, Scheduling.  The amount of Ancillary Services required may vary depending on ERCOT System conditions from hour to hour.

By 0600 of the Day Ahead, ERCOT will post an ERCOT System and zonal Load forecast for the next seven (7) days, by hour.  ERCOT will notify each QSE of its allocated share of Ancillary Services for each hour for the next day, as specified in Section 4, Scheduling.  ERCOT will make available to Market Participants any ERCOT area Load forecasts used in the determination of its ERCOT System and zonal forecasts.

ERCOT will determine the total required amount of each Ancillary Service using the Operating Guides and the following:

(1)	Balancing Energy Service:  ERCOT will estimate Balancing Energy needs based on the actual Load, the difference in forecasted Loads and Loads reported in bilateral schedules, deployed Regulation Service, and forecasted Congestion.

(2)	Regulation Service:  ERCOT will use its operational judgment and experience to determine the quantity of Regulation Up Service and Regulation Down Service procured.  The quantity of Regulation Up Service may differ from the quantity of Regulation Down Service in any particular hour.

(3)	Responsive Reserve Service:  The requirement for Responsive Reserve Service is specified in the Operating Guides.  Using ERCOT-approved procedures ERCOT may increase the quantity requirement based on its judgment of reliability conditions.

(4)	Non-Spinning Reserve Service:  ERCOT will use its operational judgment and experience to determine the quantity of Non-Spinning Reserve Service procured.

(5)	Replacement Reserve Service:  Replacement Reserve Service is procured from Generation Resource units planned to be Off-line and LaaRs that are available for interruption during the period of requirement.  The QSE for a procured RPRS Resource must additionally make available to ERCOT via Balancing Energy Service bid(s) (i) for a Generation Resource, a quantity greater or equal to the High Sustainable Limit (if unavailable, the High Operating Limit) minus the Low Sustainable Limit (if unavailable, the Low Operating Limit) of the Generation Resource receiving the RPRS Dispatch Instruction in the Congestion Zone of the Generation Resource, and (ii) for a LaaR, a quantity equal to the amount of procured capacity from the LaaR in the Congestion Zone of the LaaR.  ERCOT will consider the Generation Resource capacity On-line, based on Resource Plans, in its determination of Zonal Congestion and Local Congestion requirements.  ERCOT will evaluate the need for Replacement Reserve Service necessary to correct for ERCOT total capacity insufficiency, Zonal Congestion, or Local Congestion.  ERCOT shall determine the amount of RPRS to provide sufficient capacity in appropriate locations to provide ERCOT System security as specified in the Operating Guides, given ERCOT forecasted Load conditions as posted on the Market Information System.

(6)	Voltage Support:  ERCOT in coordination with the TDSPs shall conduct studies to determine the normally desired Voltage Profile for all Voltage Support busses in the ERCOT System and shall post all Voltage Profiles on the Market Information System.  ERCOT may temporarily modify its requirements based on Current System Conditions.  ERCOT shall determine the amount of Voltage Support Service needed to provide sufficient reactive capacity in appropriate locations to provide ERCOT System security as specified in the Operating Guides.

(7)	Black Start Service: ERCOT shall periodically determine and review the location and number of Black Start Resources required, as well as any special transmission or voice communication needs required.  ERCOT and providers of this service shall meet the requirements as specified in the Operating Guides and in NERC policy.

6.5	Technical Requirements for Providers of Ancillary Services

Providers of Ancillary Services shall meet the general requirements specified in the subsection 6.5.1, General Technical Requirements below as well as the requirements of the specific Ancillary Service being provided, as described in Sections 6.5.2, Balancing Energy Service through 6.5.11, Zonal Out-of-Merit Energy Service.

6.5.1	General Technical Requirements

Providers of Ancillary Services shall meet the following general requirements.

6.5.1.1	Requirement for Operating Period Data for System Reliability and Ancillary Service Provision

Operating Period data will be used by ERCOT to monitor the reliability of the ERCOT System in Real Time, monitor compliance with Ancillary Service Obligations, perform historical analysis, and predict the short-term reliability of the ERCOT System using network analysis software.  Each TDSP, at its own expense, may obtain such Operating Period data from ERCOT or from QSEs.

(1)	A QSE representing a Generation Entity that has Generation Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit at a Generation Resource plant location and ERCOT will make the data available to the Generation Resource’s host TDSP (at TDSP expense):

(a)	gross or net real power;

(b)	gross or net Reactive Power;

(c)	if gross quantities are provided, the plant auxiliary Load data will also be supplied;

(d)	status of switching devices in the plant switchyard not monitored by the TDSP affecting flows on the ERCOT System;

(e)	Frequency Bias of Portfolio Generation Resources under QSE operation;

(f)	any data mutually agreed by ERCOT and the QSE to adequately manage system reliability and monitor Ancillary Service Obligations;

(g)	generator breaker status;

(h)	High Operating Limit; and

(i)	Low Operating Limit.

[PRR590: Add items (j) and (k) upon system implementation:] (j) AGC status; and (k) ramp rate.

[PRR307: Revise Section 6.5.1.1(1) and 6.5.1.1(1) (c) & (g) as follows when system change implemented.] (1) A QSE representing a Generation Entity or a Competitive Retailer that has Resources connected to a TDSP shall provide the following Real Time data to ERCOT for each individual generating unit or LaaR capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action) at a Resource plant location and ERCOT will make the data available to the Resource’s host TDSP (at TDSP expense): (c) If gross quantities are provided, the plant auxiliary Load data will also be supplied as needed to determine the net output; (g) Resource breaker status;

[PRR590: Add paragraph (2) and renumber subsequent paragraphs upon system implementation:] (2) A QSE representing Uncontrollable Renewable Resources is exempt from the requirements of Section 6.5.1.1(1)(j) and (k).

(2)	Any QSE providing Responsive Reserve and/or Regulation must provide for communications equipment to receive ERCOT telemetered control deployments of service power.

(3)	Any QSE providing Regulation Service must provide appropriate Real Time feedback signals to report the control actions allocated to the QSEs Generation Resources.

(4)	Any QSE that represents a provider of Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve using LaaR shall provide separate telemetry of the real power consumption of each LaaR providing the above Ancillary Services, the LaaR response to Dispatch Instructions for each LaaR, and the status of the breaker controlling that LaaR.  If LaaR is used as a Responsive Reserve Resource, the status of the high-set under frequency relay will also be telemetered.

[PRR307: Revise Section 6.5.1.1(3) and 6.5.1.1(4) as follows when system change implemented.] (3) Any QSE providing Regulation Service must provide appropriate Real Time feedback signals to report the control actions allocated to the QSEs Resources. (4) Any QSE that represents a provider of Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve using interruptible Load as a Resource shall provide separate telemetry of the real power consumption of each interruptible Load providing the above Ancillary Services, the LaaR response to Dispatch Instructions for each LaaR, and the status of the breaker controlling that interruptible Load. If interruptible Load is used as a Responsive Reserve Resource, the status of the high-set under frequency relay will also be telemetered.

(5)	Any QSE that represents a qualified provider of Balancing Up Load (BUL) need not provide telemetry but rather shall provide an estimate in Real Time representing the real power interrupted in response to the deployment of Balancing Up Load.

(6)	Real Time data for reliability purposes must be accurate to within three percent (3%).  This telemetry may be provided from relaying accuracy instrumentation transformers.

[PRR590: Add paragraph (7) upon system implementation:] (7) A QSE representing a combined cycle plant may aggregate the AGC and ramp rate SCADA points for the individual units at a plant location into two distinct SCADA points (AGC and ramp rate) if the plant is configured to operate as such, i.e. gas turbine(s) and steam turbine(s) are controlled in aggregate from an AGC perspective.

6.5.2	Balancing Energy Service

The Balancing Energy Service bids shall consist of Balancing Energy Service Up, Balancing Energy Service Down, and Balancing Up Load bids.  All Balancing Energy Service provider bids must be entered by the close of the Adjustment Period for the effective Operating Hour and shall become an Obligation at the close of the Adjustment Period.  However, Balancing Energy Service provider bids may be withdrawn at any time prior to the close of the Adjustment Period.  The portion of a QSE’s Balancing Energy Service Up bid deployable in one interval that may be provided by off-line Generation Resources shall be limited to no more than the aggregate of qualified output amounts from Quick Start Units which have been demonstrated via the qualification testing process described in the Operating Guides.  The QSE may utilize any remaining capacity from Quick Start Units in subsequent intervals once the Quick Start Units are On-line.

Balancing Energy Service bids shall be no greater than $1,000 per MWh and no less than 
-$1,000 per MWh for all Resources.  Any Balancing Energy Service bids greater than $1,000 per MWh or less than -$1,000 per MWh will be rejected by ERCOT.

(1)	Balancing Energy Service bids must specify Congestion Zone, the type of bid, either a Resource or a BUL used to deploy the service, a ramp rate, and service time period.

(a)	For Balancing Energy Service Up and Balancing Energy Service Down, the bid curve consists of monotonically increasing ordered pairs of dollars per megawatt hour and cumulative megawatts ($/MWh, MW).

(b)	For Balancing Up Load, the bids consist of blocks in dollars per megawatt hour and megawatts ($/MWh, MW).  If the full block cannot be deployed the bid will be bypassed.

(2)	QSEs shall provide Balancing Energy Down Service bids prior to the close of the Adjustment Period equal to or greater than the requirement according to the amounts set forth for the QSE in Section 4.5.2, Receipt of QSE’s Balancing Energy Bid Curves.

(3)	ERCOT shall place all bids received for Balancing Energy Service Up and Balancing Up Load in order from lowest bid price to highest bid price.  This combination shall be the Balancing Energy Service Up Bid Stack.  ERCOT will determine the total amount of energy bid in the stack available in sixty (60) minutes.

(4)	ERCOT will determine the required amount of Balancing Energy Service such that Regulation Service Up energy and Regulation Service Down energy is provided in each Settlement Interval.

(5)	ERCOT will plan to deploy Balancing Energy Service in each Settlement Interval in a manner that will minimize total net energy from Regulation Service.

(6)	The Balancing Energy Service deployment will be in megawatts.  The Balancing Energy Obligation shall be the power requested integrated over the interval.

(7)	ERCOT may deploy Balancing Energy Service only in the Operating Period.  ERCOT’s selection of energy from Resources for deployment shall be based on the price Merit Order of bids received and bid ramp rate and not on the expected MCPE.  The ERCOT System Operator making Balancing Energy Service decisions shall not have access to the individual Balancing Energy Service bid prices or the expected MCPE.

(8)	If the Balancing Energy Service Up Bid Stack does not overlap with the Balancing Energy Service Down Bid Stack, and ERCOT is using Balancing Energy Service Up and needs a lesser amount of Balancing Energy, ERCOT must first recall any Balancing Energy Service Up prior to deploying any Balancing Energy Service Down, unless resolving Local Congestion.

(9)	If the Balancing Energy Up bid prices are lower than Balancing Energy Down bid prices, also known as overlap, and deployment required of Balancing Energy Service would result in an MCPE within the overlap then, the Balancing Energy Up and Balancing Energy Down or a portion of each are deployed, unless resolving Local Congestion.

(10)	If ERCOT is using Balancing Energy Service Down and needs a greater amount of Balancing Energy, ERCOT must first recall any Balancing Energy Service Down prior to deploying any Balancing Energy Service Up, subject to this subsection.

(11)	If ERCOT is using Balancing Energy Service Up and needs a lesser amount of Balancing Energy, ERCOT must first recall any Balancing Energy Service Up prior to deploying any Balancing Energy Service Down, subject to this subsection.

(12)	ERCOT shall not deploy Balancing Energy Service Up and Down in the same Settlement Interval in the same Congestion Zone, unless clearing an overlap in the Balancing Energy Service Up and Balancing Energy Down bid prices, or solving Local Congestion.

(13)	ERCOT shall provide ten (10) minutes notice to the QSEs providing Balancing Energy Service Up or Balancing Energy Service Down to change deployment via the Messaging System.

[PRR601: Replace the paragraph (13) with the following upon system implementation:] (13) ERCOT shall provide Notice via the Messaging System to the QSE providing Balancing Energy Service Up or Balancing Energy Service Down to change deployment five (5) minutes prior to the start of the time at which the Resource must begin to ramp up or down.

(14)	ERCOT shall provide Notice electronically via the Messaging System to each QSE with the number of megawatts expected to be delivered as a result of Balancing Energy Service Dispatch Instructions.  The Messaging System will identify requests for Balancing Up Load.

(15)	Loads acting as a Resource and providing Balancing Energy Service must be capable of responding to ERCOT Dispatch Instructions in a similar manner to Generation Resources.  BUL is not considered to be a Load acting as a Resource.

(16)	The deployment of power shall be constrained by the bidders’ specified ramp rate except during EECP Operations.

(17)	With the exception of Balancing Up Load and Load acting as Resources providing Balancing Energy Service Up, QSEs are expected to comply with Balancing Energy Service Dispatch Instructions by ramping at a constant ramp rate, as calculated in 6.5.2(18), during a fixed ramp period starting five (5) minutes prior to the start of the target service interval and ending five (5) minutes after the start of the target service interval.

[PRR601: replace paragraph (17) with the following upon system implementation:] (17) With the exception of Balancing Up Load and LaaRs providing Balancing Energy Service Up, QSEs are expected to comply with Balancing Energy Service Dispatch Instructions by ramping at a constant ramp rate, as calculated in 6.5.2(18), during a fixed ramp period starting seven and-a-half (7.5) minutes prior to the start of the Settlement Interval covered by the Dispatch Instruction and ending seven and-a-half (7.5) minutes after the start of the Settlement Interval covered by the Dispatch Instruction.

(18)	With the exception of Balancing Up Load and Load acting as Resources providing Balancing Energy Service Up, Balancing Energy Service Dispatch Instructions, inclusive of recall instructions, by ERCOT to any QSE are constrained by the amount of energy that the QSE can deploy within the ten (10) minute ramp period at the ramp rates that are communicated to ERCOT in the QSE’s bid.  Expressed in MW/Min, the ramp rates serve as the basis for calculating the maximum change in the amount of energy that the QSE can  deploy from one fifteen (15) minute Settlement Interval to the next.  In calculating these energy amounts, ERCOT will calculate the upper and lower limits of the Balancing Energy Service Dispatch Instruction of the target Settlement Interval as follows:

| Direction of Deployment in Prior Settlement Interval | Limits to P1 |
| --- | --- |
| P0 > 0 | P0 + 10 x RRU |
| P0 > 0 | P0 – Min ( P0 / RRU, 10 ) x RRU − [ 10 – Min ( P0 / RRU, 10 ) ] x RRD |
| P0 < 0 | P0 + Min ( -P0 / RRD, 10 ) x RRD + [ 10 – Min ( -P0 / RRD, 10 ) ] x RRU |
| P0 < 0 | P0 – 10 x RRD |

Where:

P0	MW amount of Balancing Energy Service deployed by ERCOT in the previous Settlement Interval.

P1	MW amount of Balancing Energy Service deployed by ERCOT in the target Settlement Interval.

RRU 	bid ramp rate (always positive) in MW/min associated with the QSE’s Balancing Up bid for the target interval.  If RRU is not available for the target interval, ERCOT will use the most recent value of the QSE’s RRU.

RRD 	bid ramp rate (always positive) in MW/min associated with the QSE’s Balancing Down bid for the target interval.  If RRD is not available for the target interval, ERCOT will use the most recent value of the QSE’s RRD.

P1 > P0	indicates a deployment of more energy in the up direction and/or less energy in the down direction from the previous Settlement Interval to the target Settlement Interval.

P1 < P0	indicates a deployment of less energy in the up direction and/or more energy in the down direction from the previous Settlement Interval to the target Settlement Interval.

ERCOT will honor the Limits to P1, as calculated above, in determining P1.

ERCOT will calculate the constant ramp rate for the P1 deployment as [P1-P0]/10.

For settlement and instructed deviation purposes, the P1 instruction along with the constant ramp rate will be used in determining the energy deployed during the ramp period and corresponding previous and target Settlement Intervals.

[PRR601: replace paragraph (18) with the following upon system implementation:] (18) With the exception of Balancing Up Load and LaaRs providing Balancing Energy Service Up, Balancing Energy Service Dispatch Instructions, inclusive of recall instructions, by ERCOT to any QSE are constrained by the amount of energy that the QSE’s Resource can deploy within the fifteen (15) minute ramp period at the ramp rates that are communicated to ERCOT in the QSE’s bid. Expressed in MW/Min, the ramp rates serve as the basis for calculating the maximum change in the amount of energy that the QSE can deploy from one fifteen (15) minute Settlement Interval to the next. In calculating these energy amounts, ERCOT will calculate the upper and lower limits of the Balancing Energy Service Dispatch instruction of the target Settlement Interval as follows: Direction of Deployment in Prior Settlement Interval; Limits to P1. P0 > 0 and P1 > P0; P0 + 15 x RRU. P0 > 0 and P1 < P0; P0 – Min ( P0 / RRU, 15 ) x RRU – [ 15 – Min ( P0 / RRU, 15 ) ] x RRD. P0 < 0 and P1 > P0; P0 + Min ( -P0 / RRD, 15 ) x RRD + [ 15 – Min ( -P0 / RRD, 15 ) ] x RRU. P0 < 0 and P1 < P0; P0 – 15 x RRD. Where: P0 MW amount of Balancing Energy Service deployed by ERCOT in the previous Settlement Interval. P1 MW amount of Balancing Energy Service deployed by ERCOT in the target Settlement Interval. RRU bid ramp rate (always positive) in MW/min associated with the QSE’s Balancing Up bid for the target interval. If RRU is not available for the target interval, ERCOT will use the most recent value of the QSE’s RRU. RRD bid ramp rate (always positive) in MW/min associated with the QSE’s Balancing Down bid for the target interval. If RRD is not available for the target interval, ERCOT will use the most recent value of the QSE’s RRD. P1 > P0 indicates a deployment of more energy in the up direction and/or less energy in the down direction from the previous Settlement Interval to the target Settlement Interval. P1 < P0 indicates a deployment of less energy in the up direction and/or more energy in the down direction from the previous Settlement Interval to the target Settlement Interval. ERCOT will honor the Limits to P1, as calculated above, in determining P1. ERCOT will calculate the constant ramp rate for the P1 deployment as [P1-P0]/10. For settlement and instructed deviation purposes, the P1 instruction along with the constant ramp rate will be used in determining the energy deployed during the ramp period and corresponding previous and target Settlement Intervals.

(19)	The QSE’s Instructed Deviation will include the expected energy calculated using the constant ramp rate, as calculated in Section 6.5.2, Balancing Energy Service, item (18), during the ten (10) minute ramp period when complying with an ERCOT Balancing Energy Service Dispatch Instruction.

[PRR601: replace paragraph (19) with the following upon system implementation:] (19) The QSE’s Instructed Deviation will include the expected energy calculated using the constant ramp rate, as calculated in Section 6.5.2, Balancing Energy Service, item (18), during the fifteen (15) minute ramp period when complying with an ERCOT Balancing Energy Service Dispatch Instruction.

(20)	ERCOT may also use LaaRs qualified to provide Regulation, Responsive Reserve, Non-Spinning Reserve, or Replacement Reserve Services to provide Balancing Energy under the OOME instructions and pricing structure.  ERCOT shall not use Loads qualified to provide only Balancing Up Load Service under the OOME instructions and pricing structure.

(21)	The minimum number of megawatts of Balancing Energy Service that may be offered to ERCOT is one (1) MW.

(22)	In the event that there is no Zonal Congestion and all available Balancing Energy Service Up bids are deployed for an interval, ERCOT shall adjust the MCPE as described in Section 6.9.5.1, Balancing Energy Clearing Price, item (2).

(23)	Should the Bid Stack for Balancing Energy Down Service be exhausted, ERCOT may send Dispatch Instructions to select Resources for OOME Service which causes the Resources to go Off-line.

(24)	ERCOT shall automatically limit each QSE’s zonal Balancing Energy Service Up bids by the sum of the High Sustainable Limits from the Resource Plan for the Generation Resources, by zone, less the zonal Schedule for the QSE’s Resources.  Any reduction to the Balancing Energy Service Up bid shall be implemented starting with the highest priced bids.

(25)	ERCOT shall automatically limit each QSE’s zonal Balancing Energy Service Down bids by the zonal Schedule for the QSE’s Resources less the sum of the Low Sustainable Limits from the Resource Plan for the Generation Resources, by zone.  Any reduction to the Balancing Energy Service Down bid shall be to the lowest cost bids.

6.5.2.1	Balancing Energy Service Bids from Bilateral Contracts

Market Participants may enter into bilateral contracts, including entitlements to Capacity Auction Products, which allow one QSE rights to submit Balancing Energy bids (bidding QSE) to ERCOT and identify another QSE as the Balancing Energy Service provider for purposes of bid deployment (deploying QSE).  Subject to the provisions in 6.5.2, Balancing Energy Service bids may be submitted to ERCOT by a bidding QSE who will identify the deploying QSE associated with the bid curve.  ERCOT will send the Balancing Energy Service Dispatch Instructions associated with the bids to the deploying QSE.

(1)	Two QSE’s may jointly apply to ERCOT for approval that both QSE’s intend to provide Balancing Energy Service in accordance with this Section 6.5.2.1.  The QSEs shall submit to ERCOT a summary of the Balancing Energy Service, identifying (a) the bidding QSE, (b) the QSE who will be receiving the Balancing Service Dispatch Instructions from ERCOT (deploying QSE), (c) the term of the service and (d) the Congestion Zone(s) in which the energy will be delivered.

(2)	The deploying QSE must be a qualified Ancillary Service provider for Balancing Energy Service.

(3)	The bidding QSE may submit separate bid curves for Balancing Energy Service Up and Balancing Service Down for each zone for each bilateral Agreement, which provides for such service.

(4)	ERCOT will provide Notice via the Messaging System to the bidding QSE and the deploying QSE of the awards for Balancing Energy Service identifying the bidding QSE and the deploying QSE.

(5)	ERCOT will notify the bidding QSE and the deploying QSE of the deploying QSE’s instructed amount of Balancing Energy Service in accordance with Section 6.7.1.1.

(6)	ERCOT will settle with the deploying QSE in accordance with Section 6.8.1.12.

6.5.3	Regulation Service (RGS)

(1)	The QSE’s control system must be capable of receiving digital control signals from ERCOT’s control system, and of directing its units to respond to the control signals, in an upward and downward direction to balance Real Time Demand and Resources, consistent with established NERC and ERCOT operating criteria.

(2)	Any QSE providing RGS must provide for communications equipment to receive telemetered control deployments of power from ERCOT.

(3)	QSEs must demonstrate to ERCOT that they have the capability to switch control to constant frequency operation as specified in the Operating Guides using telemetry at the QSE’s control center.  ERCOT authorized operations of the QSEs regulation control system on constant frequency will be considered a Dispatch Instruction to deviate from schedule energy.

(4)	QSEs providing RGS will be required to provide a feedback signal meeting the requirements of ERCOT.

(5)	The Resource providing RGS must be capable of delivering the full amount of regulating capacity offered to ERCOT within ten (10) minutes.

(6)	The minimum amount of RGS that may be offered to ERCOT is one (1) MW.

(7)	QSE’s bids will be in accordance with Section 4, Scheduling.

(8)	Regulation instructions will be included in a QSEs SCE calculation as instructed deviations.

(9)	Each Generation Resource providing RGS must meet additional technical requirements specified in Section 6.10 Ancillary Service Qualification, Testing and Performance Standards of these Protocols.

(10)	Generation Resources providing RGS must have their governors in service.

(11)	RGS is deployed proportionately to all providers.

(12)	Resources providing RGS must have sufficient qualified Generation Resources that will be On-line and able to respond in the Operating Hour for which they have been selected to provide the Ancillary Service.

[PRR307: Revise Section 6.5.3 as follows when system change implemented.] 6.5.3 Regulation Service (RGS) (1) The QSE’s control system must be capable of receiving digital control signals from ERCOT’s control system, and of directing its Resources to respond to the control signals, in an upward and downward direction to balance Real Time Demand and Resources, consistent with established NERC and ERCOT operating criteria. (2) Any QSE providing RGS must provide for communications equipment to receive telemetered control deployments of power from ERCOT. (3) QSEs must demonstrate to ERCOT that they have the capability to switch control to constant frequency operation as specified in the Operating Guides using telemetry at the QSE’s control center. ERCOT authorized operations of the QSEs regulation control system on constant frequency will be considered a Dispatch Instruction to deviate from schedule energy. (4) QSEs providing RGS will be required to provide a feedback signal meeting the requirements of ERCOT. (5) The Resource providing RGS must be capable of delivering the full amount of regulating capacity offered to ERCOT within ten (10) minutes. (6) Load Resources providing RGS must be capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and immediately responding proportionally to frequency changes (similar to generator governor action). (7) The minimum amount of RGS that may be offered to ERCOT is one (1) MW. (8) QSE’s bids will be in accordance with Section 4, Scheduling. (9) Regulation instructions will be included in a QSEs SCE calculation as instructed deviations. (10) Each Resource providing RGS must meet additional technical requirements specified in Section 6.10 Ancillary Service Qualification, Testing and Performance Standards of these Protocols. (11) Resources providing RGS must have their governors or automatic systems changing Load responding to frequency in service. (12) RGS is deployed proportionately to all providers. (13) Resources providing RGS must have sufficient qualified Generation Resources that will be online and able to respond in the Operating Hour for which they have been selected to provide the Ancillary Service.

6.5.4	Responsive Reserve Service

(1)	Responsive Reserve Service (RRS) may be provided by:  (a) unloaded Generation Resources that are On-line, (b) Resources controlled by high-set under-frequency relays, (c) hydro Responsive Reserves, or (d) from DC Tie response that stops frequency decay.  The minimum amount of RRS provided by Generation Resources shall be as specified in the Operating Guides.  QSE’s Generation Resources providing RRS must be On-line and capable of ramping to the awarded output level within ten (10) minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment.  The amount of RRS on an individual Generation Resource may be further limited by requirements of the Operating Guides.

(2)	A QSE’s Load acting as a Resource must be loaded and capable of unloading the scheduled amount of RRS within ten (10) minutes of instruction by ERCOT and by action of under-frequency relays as specified by the Operating Guides.

(3)	Any QSE providing RRS must provide communications equipment to receive ERCOT telemetered control deployments of power.

(4)	Generation Resources providing RRS must have their governors in service.

(5)	Loads acting as a Resource providing RRS must provide a telemetered output signal, including breaker status and status of the under-frequency relay.

(6)	The minimum amount of RRS that may be offered to ERCOT is one (1) MW.

(7)	QSEs that provide the Resource for Responsive Reserve Service must ensure that Resources providing the service must be able to respond in the Operating Hour for which they have been selected to provide the RRS.  Each Generation Resource and Load acting as a Resource and providing RRS must meet additional technical requirements specified in Section 6.10, Ancillary Service Qualification, Testing, and Performance Standards of these Protocols.

(8)	The amount of Resources on high-set under-frequency relays providing RRS will be limited to fifty percent (50 %) of the total ERCOT RRS requirement.  ERCOT may reduce this limit if it believes that this amount will have a negative impact on reliability or if this limit would require additional Regulation to be deployed as prescribed in Section 6.4.1, Standards for Determining Ancillary Services Quantities.

(9)	The amount of RRS that a QSE can self-arrange using Load acting as a Resource is limited to the lower of: (1) the fifty percent (50%) limit set by these Protocols, or, (2) the limit established by ERCOT.  However, a QSE may bid additional Load acting as a Resource above the percentage limitation established by ERCOT for sale of RRS to other Market Participants.   The total amount of Responsive Reserve Service using Load acting as a Resource procured by ERCOT is also limited to the lesser of the fifty percent (50%) limit or the limit established by ERCOT.

(10)	QSE bids for RRS will be in accordance with Section 4, Scheduling.

(11)	A Load acting as a Resource has the option to request a Load bid to be deployed only as a complete block.  To the extent that ERCOT deploys a bid by a Load acting as a Resource that has chosen a block deployment option, ERCOT shall either deploy the entire bid or, if only partial deployment is possible, skip the bid by the Load acting as a Resource and proceed to deploy the next available bid.

(12)	The amount of RRS that a QSE can self-arrange using Load acting as a Resource is limited to the percentage amount of total RRS that the LaaR can provide as specified by ERCOT.  However, a QSE may bid additional Load acting as a Resource into the ERCOT RRS Ancillary Service market.

[PRR307: Revise Section 6.5.4(1), (2) & (5) as follows when system change implemented.] 6.5.4 Responsive Reserve Service (1) Responsive Reserve Service (RRS) may be provided by: (a) unloaded Generation Resources that are On-line, (b) Resources controlled by high-set under-frequency relays, (c) hydro Responsive Reserves, (d) from DC Tie response that stops frequency decay or, (e) from Load Resources capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action). The minimum amount of RRS provided by Generation Resources and Load Resources capable of controllably reducing or increasing consumption under Dispatch control (similar to AGC) and that immediately respond proportionally to frequency changes (similar to generator governor action) shall be as specified in the Operating Guides. QSE’s Resources providing RRS must be On-line and capable of ramping to the awarded output level within ten (10) minutes of the notice to deploy energy, must be immediately responsive to system frequency, and must be able to maintain the scheduled level for the period of service commitment. The amount of RRS on an individual Generation Resource may be further limited by requirements of the Operating Guides. (2) A QSE’s Load acting as a Resource must be loaded and capable of unloading the scheduled amount of RRS within ten (10) minutes of instruction by ERCOT and must either be immediately responsive to system frequency or be interrupted by action of under-frequency relays as specified by the Operating Guides. (5) Interruptible Loads acting as a Resource providing RRS must provide a telemetered output signal, including breaker status and status of the under-frequency relay.

6.5.5	Non-Spinning Reserve Service (NSRS)

(1)	NSRS providers must be capable of being synchronized and ramped to their bid-specified output level within thirty (30) minutes.  NSRS can be provided from unloaded On-line capacity that can ramp within thirty (30) minutes or Load acting as a Resource that is capable of unloading within thirty (30) minutes and that is not fulfilling any other commitment from the capacity, including participation in ERCOT markets, self-generation, or other energy transactions.

(2)	Loads providing NSRS must provide a telemetered output signal, including breaker status.

(3)	The minimum amount of NSRS that may be offered to ERCOT is one (1) MW.

(4)	Each Generation Resource and Load acting as a Resource and providing NSRS must meet additional technical requirements specified in Section 6.10, Ancillary Service Qualification Testing and Performance.

(5)	QSEs using Loads to provide NSRS must be capable of responding to ERCOT Dispatch Instructions in a similar manner to QSEs using Generation Resource to provide NSRS.

(6)	Resources providing NSRS must be able to respond in the hours for which they have been scheduled to provide the Ancillary Service.

(7)	QSE bids for NSRS will be submitted in accordance with Section 4, Scheduling.

6.5.6	Replacement Reserve Service

(1)	Replacement Reserve Service (RPRS) is provided by Resources that may otherwise be unavailable to ERCOT in the hours that ERCOT requests RPRS.  These Resources may include Generation Resources that are expected to be off-line in the requested hours and Loads acting as a Resource that otherwise may be unavailable to be dispatched by ERCOT, i.e.  Loads not declared as an active Resource in the Resource Plan at the time of the RPRS procurement.

[PRR307: Revise Section 6.5.6(1) as follows when system change implemented.] 6.5.6 Replacement Reserve Service (1) Replacement Reserve Service (RPRS) is provided by Resources that may otherwise be unavailable to ERCOT in the hours that ERCOT requests RPRS. These Resources may include Generation Resources that are expected to be off-line in the requested hours and Loads acting as a Resource that are declared to be available in the Resource Plan but are not committed to any service Obligation.

(2)	Resources providing RPRS must provide a telemetered output signal, including breaker status.

(3)	The minimum amount of RPRS that may be offered to ERCOT is one (1) MW.

(4)	Resources eligible to bid must meet additional technical requirements specified in Operating Guides

(5)	There may only be one RPRS bid from any given Resource.

(6)	Generation Resource and Loads acting as a Resource accepted for RPRS must be able to respond in the hours for which they have been selected to provide the Ancillary Service.

(7)	QSEs using Loads to provide RPRS must be capable of responding to ERCOT Dispatch Instructions in a similar manner to QSEs using Generation Resources to provide RPRS.

(8)	Each Generation Resource and Load acting as a Resource providing RPRS must meet additional technical requirements specified in the Ancillary Service Qualification, Testing and Performance Standards, 6.10.  QSEs must comply with their Balanced Schedule despite any generation provided by the RPRS unit.  For example, the QSE supplying RPRS must adjust other Resources to accommodate the minimum operating output of the RPRS Resource selected by ERCOT in order to comply with their Balanced Schedule and Dispatch Instructions.

(9)	QSE bids for RPRS will be in accordance with Section 4, Scheduling.

(10)	RPRS may not be self-arranged by the QSE.

6.5.7	Voltage Support Service

All Generation Resources (including self-serve generating units) that have a gross generating unit rating greater than twenty (20) MVA or those units connected to the same transmission bus that have gross generating unit ratings aggregating to greater than twenty (20) MVA, that supply power to the ERCOT Transmission Grid, shall provide Voltage Support Service.

6.5.7.1	Generation Resources Required to Provide VSS Installed Reactive Capability

(1)	Generation Resources required to provide VSS must be capable of producing a defined quantity of Reactive Power at rated capability (MW) to maintain a Voltage Profile established by ERCOT.  This quantity of Reactive Power is the Unit Reactive Limit (URL).

(2)	Generation Resources required to provide VSS except as noted below in items (3) or (4), shall have and maintain a URL which has an over-excited (lagging) power factor capability of ninety-five hundredths (0.95) or less and an under-excited (leading) power factor capability of ninety-five hundredths (0.95) or less, both determined at the generating unit's maximum net power to be supplied to the transmission grid and at the transmission system Voltage Profile established by ERCOT, and both measured at the point of interconnection to the TDSP.

(3)	Qualified renewable Generation Resources (as described in Section 14, Renewable Energy Credit Trading Program) in operation before February 17, 2004, required to provide VSS and all other Generation Resources required to provide VSS that were in operation prior to September 1, 1999, whose current design does not allow them to meet the URL as stated above, will be required to maintain a URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at its rated capability (MW) as determined using procedures and criteria as described in the Operating Guides.

(4)	New generating units connected before May 17, 2005, whose owners demonstrate to ERCOT’s satisfaction that design and/or equipment procurement decisions were made prior to February 17, 2004, based upon previous standards, whose design does not allow them to meet the URL as stated above, will be required to maintain a URL that is limited to the quantity of Reactive Power that the Generation Resource can produce at its rated capability (MW) as determined using procedures and criteria described in the Operating Guides.

(5)	Upon request to, and with the approval of ERCOT, multiple generating units connected to the same transmission bus may be treated as a single generating unit for the purposes of these URL requirements only.

(6)	Upon submission by a Generation Resource required to provide VSS to ERCOT of a specific proposal for requirements to substitute for these URL requirements, ERCOT shall either approve such alternative requirements or provide the submitter an explanation of its objections to the proposal.  Alternative requirements may include supplying additional static and/or dynamic Reactive Power capability as necessary to meet the area’s Reactive Power requirements.

(7)	Reserved

[PRR493: Replace item (7) above upon filling ERCOT staffing requirements.] (7) An induction generator may elect to make a contribution in aide of construction in lieu of meeting the installed capacity VSS requirements contained herein. In order to comply with the VSS requirements under this Section, 6.5.7.1 (7), the generator must make payment to the interconnecting TDSP under its generation Interconnection Agreement in a manner similar to that used to collect payments for the direct assignment of interconnection Facilities under applicable PUCT rules. The level of payment shall reflect the cost to the TDSP of procuring, installing, operating, and maintaining any Reactive Power equipment required to replace the Reactive Power capability that otherwise would be necessary for the interconnection of the generator. In order for this Section 6.5.7.1(7) to be effective for VSS compliance, the TDSP shall certify to ERCOT that the induction generator has complied with these requirements.

(8)	For Generation Resources required to provide VSS, no unit equipment replacement or modification shall reduce the capability of the unit below the requirements to be met by that unit prior to the replacement/modification, unless specifically approved by ERCOT.

(9)	Generation Resources required to provide VSS shall not reduce high reactive loading on individual units during abnormal conditions without the consent of ERCOT (conveyed by way of their QSE) unless equipment damage is imminent.

6.5.7.2	QSE Responsibilities

(1)	QSE Generation Resources required to provide VSS are expected to have and maintain Reactive Power capability at least equal to the Reactive Power capability requirements specified in these Protocols and the Operating Guides.

(2)	Each QSE’s Generation Resource providing VSS is expected to be compliant with the Operating Guides for response to transient voltage disturbance.

(3)	Each Generation Resource providing VSS must meet technical requirements specified in Section 6.10, Ancillary Service Qualification, Testing and Performance Standards.

(4)	Each QSE’s Generation Resource providing VSS shall operate with the unit’s Automatic Voltage Regulator (AVR) set to regulate generator terminal voltage in the voltage control mode unless specifically directed to operate in manual mode by ERCOT, or when the unit is going On- or Off- line.  If the QSE changes the mode, other than under ERCOT direction, then the QSE shall promptly inform ERCOT. Any QSE-controlled power system stabilizers will be kept in service unless specifically permitted to operate otherwise by ERCOT.  QSEs’ control centers will monitor the status of their regulators and stabilizers, and shall report abnormal status changes to ERCOT.

(5)	QSEs shall meet, within established tolerances, and respond to changes in the Voltage Profile established by ERCOT subject to the stated QSE Reactive Power and actual power operating characteristic limits and voltage limits.

(6)	The reactive capability required must be maintained at all times the plant is On-line.

(7)	QSE shall advise ERCOT Operations whenever their Generation Resources are not operating at a power factor level as specified in the Operating Guides.  Upon such notice, ERCOT Operations, in conjunction with the appropriate TSP, shall investigate the situation with the goal of restoring the reported unit’s operation to within the specified power factor range.  Actions that ERCOT may take include the addition or removal of transmission reactive devices to/from service or a request to another Generator Resource within electrical proximity for the production of leading or lagging VARS (as appropriate) so as to equitably share the need for voltage support among Generation Resources.  Requests arising within the context of this subsection may not result in the operation of a Generation Resource outside of the specified reactive operating range.  Accordingly, Generation Resources are expected to voluntarily comply with these requests.  Nothing in this subsection is meant to supersede ERCOT’s Dispatch authority in the event of emergency operations.

6.5.7.3	ERCOT Responsibilities

(1)	ERCOT, in coordination with the TDSPs, shall establish, and update as necessary, Voltage Profiles at points of interconnection of Generation Resources required to provide VSS to maintain system voltages within established limits.

(2)	ERCOT shall communicate to the QSE and the TDSPs the desired voltage at the point of generation interconnection by providing Voltage Profiles.

(3)	ERCOT, in coordination with the TDSPs, shall deploy static Reactive Power Resources as required to continuously maintain dynamic Reactive Reserves from QSEs, both leading and lagging, adequate to meet ERCOT System requirements.

(4)	For any Market Participant’s failure to meet the Reactive Power voltage control requirements of these Protocols, ERCOT shall notify the Market Participant in writing of such failure and, upon a request from the Market Participant, explain whether and why the failure must be corrected.

(5)	ERCOT shall notify all affected TDSPs of any alternative requirements it approves pursuant to Section 5.2.1, Standards and Practices.

6.5.8	Black Start Service

(1)	Providers of Black Start Service shall meet the requirements specified in NERC policy and Operating Guides.

(2)	Each Resource providing Black Start Service must meet technical requirements specified in Section 6.10, Ancillary Service Qualification, Testing and Performance Standards.

(3)	Beginning in 2001, ERCOT will request bids from Generation Resource Entities for the provision of Black Start Service.  Such bids shall be due on or before June 1 of each year.  Bids will be evaluated based on evaluation criteria attached as an appendix to the request for bids and contracted by December 31 for the following calendar year.  ERCOT shall ensure Black Start Services are arranged, provided, and deployed as necessary to reenergize the ERCOT System following a total or partial system blackout.

(4)	ERCOT shall schedule random testing or simulation, or both, to verify Black Start Service is operable according to the ERCOT System restoration plan.  Testing and verification will be in accordance with established qualification criteria.

(5)	QSEs representing Generation Resources contracting for Black Start Services shall participate in training and restoration drills coordinated by ERCOT.

(6)	ERCOT shall periodically conduct system restoration seminars for all TDSPs, QSEs, Generation Entities and other Market Participants.

6.5.9	Reliability Must-Run Service

(1)	Upon receiving Notice from a Generation Entity as described in Protocols Subsection 6.5.9.1, Application and Approval of RMR Agreements, ERCOT may enter into RMR Agreements and begin procurement of RMR Service according to the provisions of this section.

(2)	Before entering into an RMR Agreement, ERCOT shall assess alternatives to the proposed RMR Agreement.  The list of alternatives ERCOT should consider include (as reasonable for each type of reliability concern identified):

a)	redispatch/reconfiguration through operator instruction;

b)	Remedial Action Plans;

c)	special protection schemes initiated on unit trips or transmission outages; and

d)	Load response alternatives once a suitable Load response service is defined and available.

(3)	ERCOT shall reasonably attempt to minimize the use of RMR Facilities.  ERCOT shall have the right to Dispatch an RMR Unit at any time for transmission reliability.  ERCOT will Dispatch the unit as early as possible once conditions are identified that require the use of the RMR Unit, as defined in Section 4, Scheduling and the RMR Agreement.

(4)	Each RMR Unit must meet technical requirements specified in Section 6.10 Ancillary Services Qualification, Testing and Performance Standards.

(5)	RMR Service is a contracted service between Generation Entities and ERCOT.  The term of any RMR Agreement shall not exceed 12 months except where a Generation Entity must make a significant capital expenditure to meet environmental regulations or to ensure availability in order to continue operating the unit so as to make an RMR Agreement in excess of 12 months appropriate, in ERCOT’s opinion.  The term of a multi-year RMR Agreement shall reflect the RMR Replacement Option determined in Section 6.5.9.1, Initiation and Approval of RMR Agreements, item (11).  The RMR Standard Agreement is included in Section 22, Protocols Agreements.

(6)	A Generation Resource is eligible for RMR status based on criteria established by ERCOT indicating its operation is necessary to support ERCOT System reliability.  A combined cycle Facility will be treated as a single unit for RMR purposes unless the combustion turbine and the steam turbine can operate separately.  If the steam turbine and combustion turbine can operate separately, and the steam turbine is powered by waste heat from more than one combustion turbine, the combustion turbine(s) accepted for RMR Service and a proportionate portion of the steam turbine will be treated as a single unit for RMR purposes.  If the combustion turbine accepted for RMR Service can operate separately from the steam turbine, and only the combustion turbine is accepted as an RMR Unit, the RMR Energy Price will be reduced by the value of the combustion turbine’s waste heat calculated at the Gas Price Index, except when the steam turbine is off-line.  ERCOT shall post the criteria upon which it evaluates whether an RMR Unit meets the test of operational necessity to support ERCOT System reliability.  A Generation Entity can obtain RMR Agreements only where necessary to ensure ERCOT System reliability according to the Operating Guides.

(7)	A Generation Entity cannot be compelled to enter into an RMR Agreement.  Owners of Generation Resources that are uneconomic to remain in service can voluntarily petition ERCOT for contracted RMR status by following the process in Subsection 6.5.9.1, Application and Approval of RMR Agreements.  ERCOT will be required to determine whether the unit is necessary for system reliability based on the criteria set forth in Subsection 6.5.9(6).  If ERCOT determines that the nominated unit is required for system reliability, the Generation Entity may request ERCOT to allow operation as a Synchronous Condenser in place of RMR operation.  If Synchronous Condenser operation is offered by the Generation Entity, ERCOT shall accept Synchronous Condenser operation unless ERCOT reasonably determines that a Synchronous Condenser operation is not adequate to meet system reliability according to the Operating Guides.

(8)	ERCOT must contract for the entire capacity of each RMR Unit.

(9)	RMR Units may not participate in the bilateral capacity and energy markets, including Self-Arranged Ancillary Services.  RMR Units may participate in the Balancing Energy Service market during times when ERCOT has requested the RMR Unit to run at less than full capacity, provided such participation does not limit availability to ERCOT to less than the Operational and Environmental Limitations as described in the RMR Agreement.  ERCOT will endeavor to Dispatch an RMR Unit prior to procuring OOMC, OOME, or Zonal OOME Services from other Generation Entities, if economic to do so, based on ERCOT’s knowledge at the time, and provided that the RMR Unit supplies equivalent reliability support as would the OOMC, OOME, or Zonal OOME Service, and further provided that the availability constraints of the RMR Unit are maintained.  Within two (2) weeks following any month in which an RMR Unit is dispatched, the owner/operator of the RMR Unit will inform ERCOT of the RMR Unit’s remaining availability.

(10)	RMR Units are dispatched by ERCOT when necessary to provide ERCOT System security, including any emergency situation.

(11)	ERCOT will treat the undeployed energy from RMR Units like any other unit for purposes of Balancing Energy Service Up provided the time of use constraints of the RMR Unit are maintained.

(12)	ERCOT will administer RMR Agreements in such a way as to minimize the use of RMR Units as much as practicable.  ERCOT will provide to all Market Participants all information relative to the use of RMR Units including energy deployed.

(13)	The Generation Entity which owns the RMR Unit may not use the RMR Unit for:

(a)	Participation in the bilateral energy market;

(b)	Self-provision of energy except for plant auxiliary Load obligations under the RMR Agreement;

(c)	Provision of Self Arranged Ancillary Services to any Entity; and

(d)	Ancillary Services markets, except for incremental bids into the Balancing Energy Services market to the extent allowed in the RMR Agreement.

6.5.9.1	Initiation and Approval of RMR Agreements

(1)	Except for the occurrence of a Forced Outage, a Generation Entity must notify ERCOT in writing no less than ninety (90) days prior to the date on which the Generation Entity intends to cease or suspend operation of a Generation Resource for a period of greater than one hundred eighty (180) days by submitting a completed Part I of the Notification of Suspension of Operations (“Notification”) (Found in Section 22, Attachment I, Notification of Suspension of Operations). The Generation Entity may also complete Part II of the Notification and submit it along with Part I, or may wait to submit Part II until ERCOT makes an initial determination of the need for the Generation Resource as RMR.  The Part I Notification must include a corporate officers’ attestation that a Generation Resource is uneconomic to remain in service and will be unavailable for Dispatch by ERCOT for a period specified in the Notification.  The “Minimum Agreement Period” shall be the one hundred eighty (180) day period from November 1 through April 30.  ERCOT may execute RMR Agreements for the Minimum Agreement Period or for a term of one year, except as provided in Section 6.5.9, Reliability Must Run Service, item (5).  At least sixty (60) days before the expiration of an existing RMR Agreement, the Generation Entity may apply to renew the RMR Agreement.  In order to apply to renew the RMR Agreement, the Generation Entity must submit a new Notification (including both Part I and Part II).

(2)	Upon receipt of the Part I Notification, ERCOT shall post on the MIS all existing relevant studies and data and ERCOT shall provide electronic Notice to all Registered Market Participants of the Notification.

(3)	Within fourteen (14) days, following the postings described in Subsection 6.5.9.1(2), above, unless otherwise notified by ERCOT that a shorter comment period is required, Market Participants may submit comments to ERCOT on whether the Generation Resource meets the test of operational necessity to support ERCOT System reliability as described in Subsection 6.5.9, Reliability Must Run Service, item (4).  ERCOT shall consider and post all submitted comments on the MIS.

(4)	Within eighteen (18) days of receiving Notification, ERCOT will make an initial determination of whether the Generation Resource is required to support ERCOT System reliability.  ERCOT will post this determination on the MIS and notify the Generation Entity of the determination.

(5)	Within ten (10) days of a determination by ERCOT that the Generation Resource is required to support ERCOT System reliability, the Generation Entity shall complete Part II of the Notification of Suspension of Operations (Found in Section 22, Attachment I, Notification of Suspension of Operations). Upon receipt of Part II, ERCOT and the Generation Entity shall begin good faith negotiations on an RMR Agreement. ERCOT shall post the Part II information on the MIS.

(6)	Within sixty (60) days of receiving the Part I Notification, ERCOT will make a final assessment of whether the Generation Resource is required to support ERCOT System reliability.  If ERCOT determines that the Generation Resource is required, and the RMR Agreement between ERCOT and the Generation Resource has not yet been finalized, good faith negotiations will continue.  If ERCOT determines that the Generation Resource is not needed to support ERCOT System reliability, then the Generation Resource may cease or suspend operations according to the schedule in its Notification.

(7)	If, after ninety (90) days following ERCOT’s receipt of the Part I Notification, either ERCOT has not informed the Generation Entity that the Generation Resource is not needed for ERCOT System reliability or both parties have not signed a RMR Agreement for the Generation Resource, then the Generation Entity may file a complaint with the PUCT pursuant to P. U. C. Subst. R. 25.502(f)(1), Substantive Rules Applicable To Electric Service Providers.

(8)	If, after ninety (90) days following receipt of the Part I Notification, ERCOT and the Generation Entity have not finalized an RMR Agreement for a Generation Resource that ERCOT has determined to be required for ERCOT System reliability, then the Generation Entity shall maintain the Resource so that it is available for OOM Dispatch Instructions until no longer required to do so pursuant to P. U. C. Subst. R. 25.502(f)(2).

(9)	After conducting the analysis required by these Protocols and after the date on which it executes an RMR Agreement, ERCOT shall provide Notice to the Board, at the next Board meeting after ERCOT has signed the RMR Agreement, that the following steps have been completed with respect to any RMR Agreement signed by ERCOT:

(a)	The Generation Entity provided a complete and timely Notification including a sworn attestation supporting its claim of pending plant closure.

(b)	ERCOT received all the data requested from the applicant necessary to evaluate the need for and provisions of the RMR Agreement.  Such information was posted on the MIS by ERCOT, as it became available to ERCOT and no later than prior to execution of the RMR Agreement;

(c)	The recommended RMR Agreement is consistent with the ERCOT Protocols; and

(d)	ERCOT evaluated:

(i)	The reasonable alternatives to a specific RMR Agreement that exist and compared the alternatives against the feasibility, cost and reliability impacts of the proposed RMR Agreement;

(ii)	The timeframe in which ERCOT expects each unit to be needed for reliability; and

(iii)	The specific type/scope of reliability concerns identified for each potential RMR Unit.

(10)	ERCOT shall post on the MIS as they become available, unit-specific studies, reports, and data, by which ERCOT justifies entering into the RMR Agreement.

#### 6.5.9.2	Exit Strategy from an RMR Agreement

(1)	No later than ninety (90) days following the execution of an RMR Agreement, ERCOT shall report to the Board and post on the MIS a list of feasible alternatives that may, at a future time, be more cost-effective than the continued renewal of the existing RMR Agreement.  Through the normal ERCOT System planning process, ERCOT shall develop a list of potential alternatives to the service provided by the RMR Unit.  At a minimum, the list of potential alternatives that ERCOT shall consider include, but are not limited to, construction of new or expansion of existing Transmission Facilities, installation of voltage control devices, solicitation or auctions for interruptible Load from Retail Electric Providers, or extension of the existing RMR Agreement on an annual basis.  If a cost-effective alternative to the service provided by the RMR Unit is identified, ERCOT shall provide a proposed timeline to study and/or implement the alternative.

(2)	ERCOT shall provide reasonably available information that would enable potential MRA Resources to assess the feasibility of submitting a proposal to provide a more cost-effective alternative to an RMR Unit through the regional planning process, including any known minimum technical requirements and/or operational characteristics required to eliminate the need for the RMR Unit.  TAC shall review the output of the Regional Planning process and provide guidance prior to entering into the MRA.

(3)	Subsequent to the process identified in (2) above, ERCOT may negotiate a contract for an MRA Resource that:

(a)	technically provides an acceptable solution to the reliability concern that would otherwise be solved by the RMR Unit(s);

(b)	will provide a more cost-effective alternative to continued service by the RMR Unit (evaluated over the exit strategy period) provided, however, that no proposed MRA Resource will be considered if it does not provide at least $1 million in annual savings over the projected net annualized costs for the RMR unit; and

(c)	satisfies objective financial criteria to demonstrate that the seller is reasonably able to fulfill its performance obligations as determined by ERCOT.

(4)	If the resulting MRA Agreement would result in significantly lower total costs (on a risk adjusted basis) than continued service by the RMR Agreement, and otherwise meets the requirements of this subsection, ERCOT may execute the Agreement.  The term of the proposed MRA Agreement shall be limited to the time period until the cost-effective transmission alternative can be implemented.

(5)	If the execution of an MRA Agreement would result in the foreclosure of other technically viable solutions (e.g., the RMR Resource that is being replaced by the MRA Agreement retires and is no longer available as an alternative to the MRA Agreement), the MRA Agreement shall include terms and conditions that limit the MRA Resource owner’s ability to withdraw or raise the price of the MRA Agreement in future years until a transmission solution can be implemented.

(6)	For any MRA Agreement entered into by ERCOT, ERCOT shall annually update the list of feasible alternatives developed in Section 6.5.9.2(1) and provide an update of that information to the TAC and the ERCOT Board.

6.5.9.3	Mothballed Generation Resource Time to Service Updates

By July 1, 2005, and thereafter by April 1st of each year and when material changes occur, every Generation Entity that owns or controls a Mothballed Generation Resource or an RMR Unit with an approved exit strategy shall report to ERCOT, on a unit specific basis, the estimated lead time required for each Resource to be capable of returning to service and, in percentage terms, report probable generation capacity from each Resource that the Generation Entity expects to return to service in each Season of each of the next five (5) years.

6.5.9.4	Transmission System Upgrades Associated with an RMR and/or MRA Exit Strategy

This section applies only to RMR exit strategies corresponding to specific RMR or MRA Agreements that have not been terminated.

(1)	ERCOT and the TDSP(s) responsible for constructing upgrades to the Transmission Facilities that are part of an RMR or MRA exit strategy shall coordinate construction clearances necessary to allow timely completion of all planned Transmission Facilities upgrades.

(2)	The TDSP(s) responsible for constructing upgrades to the Transmission Facilities that are part of an RMR or MRA exit strategy shall establish and send to ERCOT estimated Outage information, including completion dates and associated model information to ERCOT per Section 8.8, Coordination for System Topology Modifications.  For purposes of this section, a Transmission Facility upgrade will be considered initiated upon the TDSP authorizing any expenditures on the upgrade including, but not limited to, material procurement, right-of-way acquisition, and regulatory approvals.

(3)	Upon initiation of the project, the TDSP(s) responsible for constructing upgrades relating to the Transmission Facilities that are part of an RMR or MRA exit strategy shall provide to ERCOT monthly updates of the project’s status, noting any acceleration or delay in planned completion date. ERCOT shall report this data through the MIS as described in Section 12.4.4.2.2, TDSP Responsibility. Within sixty (60) days of the completion date shown in the Notice provided per Section 8.8, Coordination for System Topology Modifications, for the Transmission Facilities upgrades, the TDSP will coordinate more timely updates if the timeline changes significantly.

(4)	Within ten (10) Business Days after completion of the Transmission Facilities upgrades that are part of an RMR or MRA exit strategy, ERCOT shall publish a Market Notice of such completion and the effective date of termination of the associated RMR or MRA Agreement.

6.5.9.5	RMR or MRA Contract Termination

This section applies only to RMR exit strategies corresponding to specific RMR or MRA Agreements that have not been terminated.

(1)	Once a suitable RMR or MRA exit strategy has been developed as defined in Section 6.5.9.2, Exit Strategy from an RMR Agreement, and the strategy has been approved by the ERCOT Board and the affected TDSP(s), the TDSP(s) responsible for the Transmission Facilities upgrades, when requested by ERCOT, shall submit to ERCOT:

(a)	a preliminary construction outage schedule necessary to complete the Transmission Facilities upgrades. Submissions, changes, approvals, rejections, and withdrawals regarding the preliminary construction outage schedule shall be processed through the ERCOT Outage Scheduler on the ERCOT MIS.  Such construction outage schedule shall be updated monthly; or

(b)	a CCN application timeline for projects requiring such PUCT certification.  Once a CCN has been granted by the PUCT, the TDSP(s) shall be required to meet the requirements in item (a) above.

(2)	ERCOT will review and approve or reject each construction outage schedule as provided in accordance with procedures developed by ERCOT in compliance with Protocols Section 8, Planned Outages and Maintenance Outages of Transmission and Resource Facilities.

(3)	The TDSP(s) responsible for the Transmission Facilities upgrades that are part of an RMR or MRA exit strategy shall provide to ERCOT a project status and an estimated project completion date within five (5) Business Days of ERCOT’s request.

(4)	If ERCOT determines that a mutually agreeable preliminary construction outage schedule can be accommodated during the fall, winter, or spring, ERCOT and the TDSP shall collaborate to determine if the ninety (90) day termination notice for the RMR and/or MRA can be issued as soon after the summer load season of the preceding year as possible and publish a Market Notice of these terminations.  ERCOT and the TDSP may give consideration to the risk of the decision to terminate the RMR and/or MRA Agreement and any options, such as Remedial Action Plans and/or Mitigation Plans that could be used to mitigate transmission construction delays.

6.5.9.6	RMR and/or MRA Contract Extension

This section applies only to RMR exit strategies corresponding to specific RMR or MRA Agreements that have not been terminated.

(1)	Forty-five (45) days prior to the termination date of an existing RMR or MRA Agreement, pursuant to the 90-day termination notice as described in Section 22F3A2, ERCOT shall assess the likelihood of completion of the Transmission Facilities upgrade project(s) necessary to allow termination of an existing RMR or MRA Agreement based on the updates of project status provided by the TDSP(s).  If ERCOT determines that a delay in the termination  date of the existing RMR or MRA Agreement is necessary to allow completion of the Transmission Facilities upgrade(s), it shall provide written notice to the Resource Entity that owns the RMR Unit or MRA Resource of its intent to execute an extension to the existing RMR or MRA Agreement no later than thirty (30) days prior to the planned termination date.

(2)	Forty-five (45) days prior to the expiration date of an existing RMR or MRA Agreement for which the Generation Entity has applied for renewal, ERCOT shall assess the likelihood of completion of the Transmission Facilities upgrade project(s) necessary to eliminate the reliability need for a Resource with an existing RMR or MRA Agreement based on the updates of project status provided by the TDSP(s).  If ERCOT determines that an extension of the existing RMR or MRA Agreement of no more than ninety (90) days would allow completion of the Transmission Facilities upgrade(s), it shall provide written notice to the Resource Entity that owns the RMR Unit or MRA Resource of its intent to execute an extension to the existing RMR or MRA Agreement no later than thirty (30) days prior to the planned expiration date.

(3)	ERCOT may extend the existing RMR or MRA Agreement as necessary to allow completion of the Transmission Facilities upgrade(s), but in no event shall the extension last more than ninety (90) days from the termination or expiration date of the existing RMR or MRA Agreement.

(4)	Forty-five (45) days prior to the end of the period for which the existing RMR or MRA Agreement has been extended, ERCOT shall assess whether the transmission upgrades are likely to be completed.  If ERCOT determines that the upgrades are not likely to be completed, ERCOT shall enter into negotiations with the Resource Entity that owns the RMR or MRA Resource to negotiate a new RMR or MRA Agreement to allow completion of the planned transmission upgrades.

6.5.10	Out of Merit Capacity and Out of Merit Energy Services

(1)	ERCOT will use OOMC and OOME Services to procure additional capacity and energy required to provide reliable ERCOT System operation, or to effectively manage Local Congestion as determined by ERCOT.

(2)	ERCOT may call on any Generation Resource to provide OOMC or OOME Service, in any time frame that the Resource is listed as available in its Resource Plan.  ERCOT may interrupt Loads Acting as Resources to provide OOME Service when the Load Resource is listed as available in its Resource Plan.

(3)	For combined cycle plants, or other plants that involve tandem operation of Resources, a Generation Entity may request ERCOT approval to treat the plant at which these Resources are located as an Aggregated Unit.

(4)	ERCOT may use OOMC when necessary to provide ERCOT System security and capacity adequacy.  ERCOT will Dispatch Resources for OOMC and OOME Service in such a way as to minimize the use of these services as much as practicable.

(5)	ERCOT may, at its discretion, use OOMC Service as necessary to effectively manage Local Congestion if either of the following conditions apply:

(a)	The Resource-specific deployments necessary to manage a specific Local Congestion problem are expected to use Resources that have Generation Shift Factors of less than or equal to five percent (5%) impact on the congested element; or

(b)	The total amount of Resource-specific deployments to manage a single Local Congestion situation exceeds one thousand (1,000) MW.

(6)	Consistent with Section 2.2.2 of the ERCOT Operating Guides, ERCOT will evaluate the need for Resource-specific deployments during Real Time operations for management of Local Congestion by excluding the Forced Outage of any double circuit transmission line as a credible single contingency, unless the transmission line meets the criteria of High Outage Probability or High Outage Consequence as those terms are defined in Section 4.3 of the ERCOT Operating Guides.

(7)	ERCOT will settle OOME Service in accordance with the Balancing Energy settlement provisions in Section 6.8.2.3, Energy Payments.

(8)	ERCOT may also use bids from Loads acting as Resources under the OOME Dispatch Instructions and pricing structure.

(9)	The QSE associated with Generation Resources receiving a Dispatch Instruction to provide OOMC and/or OOME Service(s) and/or LaaRs providing OOME Service(s) only must use all commercially reasonable efforts to provide the requested service(s).  If the QSE declines the Dispatch Instruction to provide OOMC and/or OOME Service(s) pursuant to the provisions of Section 5.4.4, Compliance with Dispatch Instructions, ERCOT will post such declines on the MIS.

(10)	If ERCOT Dispatches a Resource for OOMC Service to sustain reliable ERCOT System operation or effectively manage Local Congestion, the QSE receiving the Dispatch Instruction must bid into the Balancing Energy Up and Down market quantities which sum greater or equal to the High Sustainable Limit (if unavailable, the High Operating Limit) minus the Low Sustainable Limit (if unavailable, the Low Operating Limit) of the Resource receiving the OOMC Dispatch Instruction, in the Congestion Zone of the Resource that receives the OOMC Dispatch Instruction.

On or before the second (2nd) Business Day after each Operating Day, ERCOT will post on the MIS, for such Operating Day:

(a)	Each Resource receiving an OOMC Dispatch Instruction;

(b)	Intervals for which a Resource received an OOMC Dispatch Instruction; and

(c)	The Low Sustainable Limit for each Resource receiving an OOMC Dispatch Instruction.

[PRR515: Upon system implementation, insert new paragraph (d).] (d) in the case of Congestion, the binding transmission constraint (contingency and/or overloaded element(s)) causing the OOMC deployments.

(11)	For OOME Dispatch Instructions, ERCOT will post the following information on the MIS, for each Operating Day:

(a)	On or before the second (2nd) Business Day following the Operating Day on which ERCOT issued the Dispatch Instruction, each Resource receiving an OOME Up Dispatch Instruction for each interval;

(b)	On or before the second (2nd) Business Day following the Operating Day on which ERCOT issued the Dispatch Instruction, each Resource receiving an OOME Down Dispatch Instruction for each interval ;

(c)	On or before the Business Day following the day of issuance of the Initial Statement for the Operating Day on which ERCOT issued the Dispatch Instruction, as described in Section 9.2.3, Initial Statements, the amount of OOME Up provided by each Resource for each interval; and

(d)	On or before the Business Day following the day of issuance of the Initial Statement for the Operating Day on which ERCOT issued the Dispatch Instruction, as described in Section 9.2.3, Initial Statements, the amount of OOME Down provided by each Resource for each interval.

[PRR515: Upon system implementation, insert (9)(e).] (e) the binding transmission constraint (contingency and/or overloaded element(s)) causing OOME deployments shall be posted on or before the second (2nd) Business Day.

(12)	In the event that an OOME Dispatch Instruction causes a Resource to go Off-line, ERCOT shall either:

(a)	Provide the Resource’s QSE with OOME Dispatch Instructions until the Resource was scheduled to be Off-line in the current Resource Plan; or

(b)	Provide the Resource’s QSE with an OOMC Dispatch Instruction if the Resource is recalled, unless the current Resource Plan indicates that the Resource was scheduled to go Off-line, until the time that ERCOT recalls the Resource.

6.5.11	Zonal Out-of-Merit Energy Service

(1)	ERCOT will use Zonal OOME Deployments to procure additional energy required to provide reliable ERCOT System operation, as determined by ERCOT.  Zonal OOME Deployments shall not be used to bring on additional capacity.

(2)	Any QSE with Generation Resources may be called upon by ERCOT to provide Zonal OOME Service in any time frame that the Resources are listed as on line in the Resource Plan.

(3)	Zonal OOME is used by ERCOT only when necessary to provide ERCOT System security and only after other Congestion management techniques have failed to clear a Congestion problem.  ERCOT will call on Zonal OOME Service in such a way as to minimize the use of this service as much as practicable.

(4)	Zonal OOME will be settled in accordance with Section 6.8.2.5, Settlement of Zonal OOME Deployments.

(5)	The QSE associated with the Generation Resources that receives a Zonal OOME Dispatch Instruction must use all commercially reasonable efforts to provide the requested service.  If the QSE declines the Dispatch Instruction according to the provisions of Section 5.4.4, Compliance with Dispatch Instructions, of these Protocols to provide Zonal OOME Service(s), ERCOT will post such declines on the MIS.

(6)	Upon a SPS actuation the TSP shall inform ERCOT of the time of actuation.  The affected QSE(s) will receive a verbal Dispatch Instruction OOME instruction corresponding with the actuation that will last no longer than four (4) hours after the time of actuation.  If the actuation results in a unit being taken Off-line then ERCOT will proceed in accordance with the OOME Off-line Dispatch in Section 6.5.10 (12), Out of Merit Capacity and Out of Merit Energy Services.

(7)	In the event a SPS triggers a trip of a DC Tie, the QSE(s) scheduling the DC Tie shall be entitled to OOME payment based on the quantity of power being imported as defined by the amount shown in the NERC tag effective at the time of the SPS actuation.  ERCOT will proceed in accordance with OOME down Dispatch provisions in Section 6.8.2.3 (4), Energy Payments, utilizing the RCGFC category (Combined Cycle greater than 90 MW** = FIP * 5 MMBtu/MWh).  The QSE(s) scheduling the DC Tie will be entitled to OOME payments for the duration the DC Tie is Off-line up to a maximum of four (4) hours.

**	Determined by capacity of largest simple cycle combustion turbine in the train.

6.6	Selection Methodology

6.6.1	Qualified Scheduling Entity Rights and Obligations to Self-Arrange Ancillary Service Resources

(1)	QSEs may self-arrange only Regulation Up, Regulation Down, Responsive Reserve Services, and Non-Spinning Reserve Services.

(2)	A QSE may self-arrange Resources by indicating the amount of each Ancillary Services that will be self-arranged in each hour of the Operating Day.

(3)	The quantity self-arranged specified by a QSE at 1100 in the Day Ahead shall not be changed for the Day Ahead Obligation, unless ERCOT allows schedules to be updated at 1300 in accordance with Section 4.4.10, QSE Submittal of Updated Balancing Energy Schedules.

(4)	The quantity of Self-Arranged AS specified by a QSE in response to a Notice by ERCOT to obtain additional AS in the Adjustment Period cannot be greater than the allocated additional AS amount and cannot be changed once committed to ERCOT.

(5)	QSEs may schedule with ERCOT to provide Ancillary Services on another QSE’s behalf by notifying ERCOT consistent with the requirements of Section 4, Scheduling.

6.6.2	Competitive Procurement of Ancillary Service Resources by ERCOT

(1)	Except where stated to the contrary in these Protocols, ERCOT shall, to the extent the Ancillary Service Resource bids are available, use competitive procurement processes to procure sufficient Ancillary Service Resources to meet the requirements specified in these Protocols.

(2)	QSEs may submit bids to provide Regulation Down, Regulation Up, Responsive Reserves, and Non-Spinning Reserves, as part of the Scheduling Process in accordance with Section 4, Scheduling.

(3)	QSEs offering Balancing Energy Up, Balancing Energy Down, and Replacement Reserves can offer bids through the Adjustment Period, in accordance with Section 4.5, Adjustment Period Scheduling Process.

(4)	QSE’s bids to provide Ancillary Services will continue to be valid until withdrawn by the QSE prior to the market clearing or the market is cleared.  Bids may not be withdrawn during bid evaluation by ERCOT as described in Scheduling Sections 4.4 Day Ahead Scheduling Process and Section 4.5 Adjustment Period Scheduling Process or after the bid is selected.

(5)	QSEs may only submit bids from that portion of any Resource not used to provide capacity and energy to Supply the Resources in the QSE’s Balanced Schedule.

(6)	ERCOT will determine the MCPC of each interval for Regulation Up, Responsive Reserve and Non-Spinning Reserve using an optimized simultaneous selection process in order to minimize the overall cost of these Ancillary Services.

(7)	Other than as specified for Congestion Management, ERCOT shall select Replacement Reserve and Regulation Down bids based on the lowest bid for each service.

(8)	Other than as specified for Congestion Management, ERCOT shall Dispatch energy from the Balancing Energy Service bids based on price Merit Order and the requirements specified in Section 5, Dispatch Instructions.

(9)	For Congestion Management, ERCOT shall, if possible, resolve all Congestion using the Balancing Energy Service by Congestion Zone.

(10)	ERCOT shall establish, through an annual competitive procurement process, annual agreements with Resources needed to provide Black Start capability.

6.6.3	ERCOT Day-Ahead Ancillary Service Procurement Process

6.6.3.1	General Procurement Requirements

(1)	ERCOT shall conduct daily the Day Ahead bidding process for the purpose of procuring the quantities of Resources as specified in the Ancillary Services Plan for all Operating Hours of the next Operating Day to provide Regulation Up, Regulation Down, Responsive Reserves, and Non-Spinning Reserves.

(2)	ERCOT shall procure Regulation Up, Responsive Reserve and Non-Spinning Resources in the Day-Ahead market simultaneously for each hour of the next Operating Day such that the overall cost of these Ancillary Services are minimized.  ERCOT will also procure Regulation Down and Replacement Reserves, if needed, prior to the end of the Day Ahead market.

(3)	ERCOT will procure the amount of each service specified in the Ancillary Service Plan, less the amount self-arranged, without substituting one service for a different service.

(4)	A QSE may offer the same Resource capacity into any or all of the Ancillary Services markets simultaneously.  A QSE may specify different capacity bids from a single Resource for each of the Ancillary Service markets into which the Resource is bid in compliance with Section 4, Scheduling.

(5)	When the same Resource capacity is simultaneously offered for more than one of RGS Up, RRS, and NSRS, ERCOT will select the service for which the capacity will be awarded such that the overall cost of these Ancillary Services is minimized.

(6)	For each Ancillary Service procurement process, ERCOT shall select capacity bids submitted by QSEs, such that:

(a)	After adjusting for self-arranged Resources, the total amount of capacity procured by ERCOT meets the Ancillary Services Plan requirements; and

(b)	For each of RGS Up bid as well as RRS and NSRS bids will be arranged in the Bid Stack such that the overall cost of these Ancillary Services is minimized.  For each of these Ancillary Services, if selection of the marginal capacity block will exceed ERCOT’s required Ancillary Service quantity, ERCOT will select a portion of this capacity block as the actual marginal AS quantity accepted.

(c)	For RGS Down, ERCOT will procure required quantities by selecting capacity in ascending order starting from the lowest priced bid.  ERCOT will continue this selection process until the required quantity of RGS Down is obtained.

[PRR496: Revise (b) upon system implementation] (b) For each of RGS Up bid as well as RRS and NSRS bids that are not designated as block bids will be arranged in the Bid Stack such that the overall cost of these Ancillary Services is minimized. For each of these Ancillary Services, if selection of the marginal capacity block will exceed ERCOT’s required Ancillary Service quantity, ERCOT will select a portion of this capacity block as the actual marginal AS quantity accepted.

(d)	In the case where multiple bids have the same price for the selection of RGS Up, RGS Down, RRS and NSRS Ancillary Services, selection shall be awarded proportionately.

PRR496: Add (e) under Section 6.6.3.1(6) upon system implementation and Notice to the Market. (e) For RRS and NSRS bids that are designated as block bids, if the selection of the Block Bid will exceed ERCOT’s required Ancillary Service quantity the bid will be skipped and ERCOT will select the next available bid(s) as the actual marginal AS quantity accepted.

(7)	ERCOT shall deduct any Resource capacity accepted in one of the Ancillary Service procurement auctions from the capacity that is available for procurement in any subsequent Ancillary Service procurement auction if the QSE has indicated that the Resource capacity bids are linked.

(8)	ERCOT shall determine an hourly MCPC for each of the following Day-Ahead Ancillary Service markets:  Regulation Up, Regulation Down, Responsive Reserves and Non-Spinning Reserves.  The hourly MCPC shall equal the highest-priced capacity reservation bid accepted in the Day Ahead market by ERCOT for that Ancillary Service for the hour.

(9)	If the MCPC cannot be calculated by ERCOT, the MCPC for the particular Ancillary Service shall be deemed to be equal to the MCPC for that Ancillary Service in the same Settlement Period of the preceding Operating Day.

(10)	For each of RGS Up, RGS Down, RRS and NSRS, for each hour of the next Operating Day, ERCOT will post the quantity of capacity procured and the MCPC for the Day Ahead market.

[PRR558: Replace (10) above with the following upon system implementation.] (10) For each of RGS Up, RGS Down, RRS and NSRS, for each hour of the next Operating Day, ERCOT will post the quantity of capacity procured and the MCPC for the Day Ahead market. ERCOT will post a notice if the RRS awarded to LaaR was prorated for any hour.

(11)	ERCOT will be capable of using the MCPC for Non-Spinning Reserve as the MCPC for Regulation Up and/or the MCPC for Responsive Reserve.  Similarly, the MCPC for Responsive Reserve could be used for Regulation Up.  ERCOT shall not substitute prices until a determination of the conditions to allow substitution of prices from one service to another is approved by the ERCOT Board.

6.6.3.2	ERCOT Ancillary Services Procurement during Adjustment Period (AP)

During the Adjustment Period, ERCOT may procure Replacement Reserves; or as a result of changing conditions, may procure additional Regulation Up, Regulation Down, Responsive and Non-Spinning Services, as appropriate for the conditions, in order to maintain ERCOT System reliability.

ERCOT may procure Ancillary Services to replace those previously awarded to a provider who has subsequently defaulted on his Obligation.  The defaulting Entity will be financially responsible for the total cost of the Ancillary Services procured in the markets opened due to the default.

If ERCOT requires any Replacement Reserves; or additional Regulation, Responsive Reserve or Non-Spinning Reserve Services during the Adjustment Period, then ERCOT will implement the Notification process for these services in accordance with Section 4, Scheduling.

If ERCOT forecasts that there is insufficient capacity available to reliably serve system Load in any settlement period, ERCOT will implement the Notification process for Replacement Reserve Services in accordance with Section 4, Scheduling.

Additional Ancillary Services will be allocated to QSEs using the same percentages as the Day Ahead allocation except when the purchase is in the case of a default.  In this case the Ancillary Service costs shall be allocated to the defaulting Entity as provided in above.

6.6.3.2.1	Specific Procurement Process Requirements for Replacement Reserve Service in the Adjustment Period

ERCOT shall procure Replacement Reserve Service (RPRS) in the AP as follows:

(1)	ERCOT will evaluate Zonal Congestion, Local Congestion, and capacity insufficiency using ERCOT’s Operational Model, balanced QSE schedules, Resource Plans, and ERCOT forecast of next day Load.

(2)	ERCOT will define the level of Resources available to meet next-day reliability needs of the ERCOT System based on QSE schedule submissions, Resource Plans and ERCOT Load forecast.  ERCOT will determine incremental Resource capacity available from Generation Resources that are Off-line, or Generation Resources that are expected to be Off-line in the requested hours or Loads acting as a Resource shown as available in the Resource Plans.

(3)	RPRS procurement produces an optimum solution for the whole Operating Day.  The RPRS procurement resolves Local Congestion problems first and then resolves capacity inadequacy and Zonal Congestion problems simultaneously.  The solution of the RPRS is a result of ERCOT performing analysis of the current physical system operations for each hour to recognize potential transmission constraints that would require Resources not currently planned to be available.  The purpose and use of the RPRS procurement is to provide capacity from which energy would be available to solve the following system security violations:

(a)	ERCOT System capacity insufficiency using any RPRS bid;

(b)	Zonal Congestion using the RPRS bids by Congestion Zone in bid price Merit Order and the current physical system operations in the ERCOT System; and

(c)	Local Congestion using Resource Category Generic Cost and the current physical system operations in the ERCOT System.

(4)	ERCOT will solve security violations using a transmission security-constrained mathematical optimization application.  The application will solve as if each bid can be proportioned into individual MW bids.  The objective of the optimization is to minimize the total cost, based on Resource Category Generic Cost, capacity price, operation price, and Resource Shift Factors, as described in Section 4.4.16, ERCOT Receipt of Replacement Reserve Service Bids, as well as lead time, minimum up time, and minimum down time captured through the registration process, for the whole Operating Day while satisfying all the security constraints for each hour.

(5)	The costs associated with resolving system security violations will be identified separately into the following categories:  capacity inadequacy, Zonal Congestion, and Local Congestion.

(6)	The Market Clearing Prices on the capacity insufficiency, CSC constraint, and Operational Constraint will represent the marginal cost for the solution of each constraint and will be produced as an output of the mathematical optimization application.  The output of the application will be as follows:

(a)	The marginal cost (Shadow Price of the power balance constraint) to solve system insufficiency defines MCPC for insufficiency.

(b)	The marginal cost (Shadow Price of the CSC constraint) to solve a CSC constraint defines the Congestion price of the CSC constraint.

(c)	The bidder of RPRS shall be paid the higher of RPRS bid price (as defined in Section 6.8.1.10, Zonal or System Wide Replacement Reserve Service Capacity Payment to QSE) and MCPC of the Congestion Zone unless the bid has been selected to solve Local Congestion.  Resources taken to solve Local Congestion shall be paid in accordance with the Local Congestion Replacement Reserve formula in Section 6.8.1.11, Local Congestion Replacement Reserve Payment to QSE.

(7)	QSEs whose schedules have impacts on CSCs according to the Commercial Model (using zonal Shift Factors at the time of RPRS procurement for each Zone) shall be charged Congestion costs associated with the impact.

(8)	The costs of resolving Local Congestion are based on the amount of capacity required to solve Local Congestion.  This cost will be tracked by specific constraint to aid the determination of the potential addition to the constraint as a CSC.

(9)	If all of the cost of RPRS is not allocated by one of the above methods, then the allocation will be uplifted to all QSEs based on the Load Ratio Share for the relevant period.  If ERCOT collects more RPRS costs in this manner than are necessary, the excess funds collected by ERCOT will be credited to all QSEs based on the Load Ratio Share for the relevant period.

(10)	RMR Units will be considered available to offset RPRS needs in resolving Local Congestion in the RPRS procurement process.  The selection process will set a bid price for each RMR Unit based on its contract start and operational costs.  If the optimal solution indicates an RMR Unit is a more economic option in resolving Local Congestion, the RMR Unit will be deployed and paid as an RMR deployment.

Generation Resources that are eligible for RPRS procurement that do not submit an RPRS bid will be considered in the RPRS procurement process.  The selection process will set a bid price for each non-bid Generation Resource based on its generic cost times an adjustment factor.  If the non-bid Generation Resource with an adjustment factor is a more economic option, the non-bid Generation Resource will be deployed and paid as an OOMC deployment.

(11)	In the case of tied bids for the selection of RPRS, ERCOT will select the bid that meets the requirement most closely (achieving the optimal solution).  When the price and capacity are identical from unaffiliated bidders, ERCOT may request re-bids.

(12)	For RPRS, for each hour, for each Congestion Zone, ERCOT will post the quantity of capacity procured and the MCPCs and Shadow Prices.

6.6.3.3	ERCOT Emergency Ancillary Service Procurement

(1)	Any ERCOT procurement of Ancillary Services in the Operating Period other than the deployment of Balancing Energy Service will be pursuant to Section 5, Dispatch.

(2)	QSEs may not self-arrange for Ancillary Services procured in response to emergency situations.

6.6.4	Obligations to Honor Ancillary Services Commitments

The Ancillary Service Obligations from the schedule submitted prior to the close of the Adjustment Period are binding commitments of the QSE to ERCOT.  If ERCOT issues Resource-specific OOME or Resource-specific Balancing Energy Dispatch Instructions to a QSE that causes the QSE to be unable to Supply its Ancillary Service Obligation(s), the ERCOT shall issue a verbal Dispatch Instruction that:

(1)	Relieves that QSE from having to provide the specific Ancillary Service(s) for specific intervals and the reason or,

(2)	Retracts the Dispatch given to the QSE so that the QSE may come back into compliance with their Ancillary Service Obligation(s).

6.6.5	Mandatory Provision of Ancillary Service Capacity to ERCOT

Notwithstanding any other provision in these Protocols, ERCOT may require a QSE to provide OOMC, OOME, or Zonal OOME Service Resources if necessary to avoid an ERCOT System insufficiency or system Emergency Condition.  If required, ERCOT will procure these Ancillary Services in accordance with the requirements of OOMC, OOME, and Zonal OOME Services.

6.6.6	Provision of Multiple Ancillary Services from a Resource

An individual Resource may provide more than one Ancillary Service, provided that the sum of the Ancillary Service capacities committed to ERCOT, when added to the bilaterally scheduled level, is within the operating capability of the Resource as specified in the Resource Plan submitted by the QSE.

6.6.7	Insufficiency of Ancillary Services Bids

If ERCOT receives insufficient Ancillary Service bids to procure required Ancillary Services such that the Ancillary Services Plan is deficient and system security and reliability is threatened, ERCOT shall declare a market insufficiency Alert for the applicable Ancillary Service and will act in accordance with Section 5.6.5, Alert to obtain adequate Resources to ensure reliability.  If insufficiency is declared for a particular Ancillary Service in a specific hour, the market for that Service for that hour is closed.

6.6.7.1	Procurement of Ancillary Services During Insufficiency

Upon declaration of market insufficiency, ERCOT will procure and/or arrange for additional capacity of the insufficient Ancillary Service for the affected hourly intervals.  ERCOT will not accept any additional bids for the Ancillary Service for which market insufficiency has been declared.  Compensation for capacity for Ancillary Services procured during market insufficiency and for subsequent procurement after the declaration of market insufficiency will be as per Section 6.8.1.1, Payments for Ancillary Services.

6.7	Deployment Policy

Energy from Ancillary Services may be deployed by ERCOT, only in the Operating Period, and only for reliability reasons in order to maintain frequency and system security.  Energy will be deployed from Ancillary Services as prescribed by their specific function and may not be used to substitute for other services because of price except as permitted under 6.6.3.1 (10).  ERCOT shall deploy all services other than Regulation in a minimum of one (1) Mw blocks.

6.7.1	Deployment of Balancing Energy

6.7.1.1	Creation of the Balancing Energy Bid Stack

(1)	The Balancing Energy Service Bid Stack for the Operating Period will be created at the close of the Adjustment Period from the most recent Balancing Energy Service Up, Balancing Up Load, and Balancing Energy Service Down bids submitted by QSEs.  QSEs can submit revised bids up to the close of the Adjustment Period.

(2)	ERCOT may use varying amounts of Balancing Energy for each Settlement Interval as constrained by:

(a)	The QSE-designated bid ramp rate limiting the amount of Balancing Energy Service that can be deployed in each fifteen (15) minute Settlement Interval for Balancing Energy Service Up or Down bids; or

(b)	The QSE-designated block bid for Balancing Up Load.

(3)	QSEs may designate the amount of Balancing Energy Service that can be deployed in each of the Settlement Interval by:

(a)	Specifying a bid ramp rate effective for the whole hour.  The limit for the hour is no less than the total amount bid by the QSE; and/or

(b)	Designating the amount of Balancing Up Load that can be deployed by specifying blocks.

Ten minutes prior to crossing the hour boundary, ERCOT will evaluate the Balancing Energy previously awarded and re-deploy services based on specified bids for the new hour.

(4)	QSEs may:

(a)	Supply multiple price-quantity pair bids for Balancing Energy Service Up and Balancing Energy Service Down energy (i.e., “up and/or down curves”) to ERCOT for each Congestion Zone; and/or

(b)	Supply multiple block bids for Balancing Up Load Service to ERCOT for each Congestion Zone.

(5)	The MCPE for each Settlement Interval for each Congestion Zone will be posted by ERCOT to the marketplace when energy is deployed or recalled.  For Settlement Interval during which no Balancing Energy is deployed or recalled, the MCPE is the first (highest) Balancing Energy Service Down bid price for the interval.

(6)	ERCOT will develop a forecast of Balancing Energy Service needed in each Settlement Interval.

(7)	ERCOT’s System Operator will not have access to individual bid prices or the expected MCPE if the next energy bid is selected.  Rather, the Operator will deploy all or a portion of a bid, moving up and down the deployment energy stack.  All bids will remain in one stack and the MCPE will be posted, unless there is Congestion.  If energy stacks must be separated by Congestion Zone, because of Zonal Congestion, the MCPE of each zone will be posted.

(8)	ERCOT will provide Notice to QSEs via the Messaging System of their awards for Balancing Energy Service, identifying awards that are for Balancing Up Load.  QSEs will be required to respond with manual or electronic acknowledgement.

(9)	ERCOT shall notify each QSE of its instructed amount of Balancing Energy Service ten (10) minutes prior to the Settlement Interval in which it is to be deployed.  For Balancing Energy bid on Resources other than Balancing Up Loads, QSEs shall be expected to provide a power level during the Settlement Interval that will provide the instructed amount of Balancing Energy Service for that interval.  For ERCOT Instructions to deploy Balancing Up Loads, the QSE shall be expected to provide the instructed amount of Service by interrupting Load.  For ERCOT Instructions to deploy Balancing Up Loads from a QSE’s Dynamically Scheduled Load, QSEs shall be expected to ensure that the generation following the Load is increased above the actual Dynamically Scheduled Load meter readings by the amount of the signal sent to ERCOT that is estimated in Real Time representing the real power interrupted in response to the deployment of Balancing Up Load (BUL).  Deployment of energy as a result of adjustments in Dynamic Schedules to account for deployment of BUL will not be considered an Uninstructed Deviation.

(10)	Any energy provided by a QSE in a Settlement Interval in which it has not been instructed to provide Balancing Energy Service by ERCOT will not set the MCPE, regardless of whether the energy provided was necessary for the QSE to meet ERCOT’s instruction for a future or past Settlement Interval.

(11)	A Load acting as a Resource has the option to request a Load bid to be deployed only as a complete block.  To the extent that ERCOT deploys a bid by a Load acting as a Resource that has chosen a block deployment option, ERCOT shall either deploy the entire bid or, if only partial deployment is possible, skip the bid by the Load acting as a Resource and proceed to deploy the next available bid.

6.7.1.2	Deployment of Balancing Energy when Congestion Occurs

(1)	If the Operational Model indicates there is Zonal Congestion, ERCOT will separate the Balancing Energy Service bids into a Bid Stack for each Congestion Zone.

(2)	ERCOT will use the Operational Model to determine the amount and location of Balancing Energy deployment for clearing Zonal Congestion as well as balancing the system.

(3)	Except as stated in item (4) below, ERCOT will deploy Balancing Energy bids within a zone in bid price Merit Order.

(4)	ERCOT may form specific Resource prices for both incrementing and decrementing a specific Resource to resolve Local Congestion.

(5)	As part of the submittal of the Resource Plan for each Resource at a plant, QSEs may specify bid premiums by Resource.  For each Resource, a submitted bid premium for Balancing Energy Up must be less than or equal to the Resource Category Generic Price for Balancing Energy Up deployments; the submitted bid premium for Balancing Energy Down must be greater than or equal to the Resource Category Generic Price for Balancing Energy Down deployments calculated pursuant to Section 4.4.20, Posting of Resource Category Bid.  With the exception of eligible non-bid Resources [as defined in item (6) below], if a bid premium is not specified in the Resource Plan, ERCOT will set the incremental bid premium equal to the Resource Category Generic bid limit for Balancing Energy Up and the decremental bid premium equal to the Resource Category Generic bid limit for Balancing Energy Down.  Resource-specific incremental prices will be the incremental bid premium specified by the QSE based on the Resource Category Generic Price for Balancing Energy Up and the Resource-specific decremental prices will be the decremental premium specified by the QSE based on the Resource Category Generic Price for Balancing Energy Down.

(6)	A QSE may specify within the Resource Plan that Renewable Resources, Qualifying Facilities, and Loads Acting as a Resource are “non-bid Resources.”  A QSE must specify an RMR unit, a hydroelectric unit, and a nuclear unit as a non-bid Resource.  With the exception of hydroelectric and nuclear units, a non-bid Resource may be deployed automatically by the system as necessary to maintain reliability.  To accomplish this, the system will set an incremental price for the non-bid Resources such that the pricing order from lowest to highest for deployment of Balancing Energy Up among the non-bid Resources will be as follows:  RMR, Qualifying Facility, Renewable, Load Acting as a Resource.  The system will set a decremental price for the non-bid Resources such that the pricing order from lowest to highest for deployment of Balancing Energy Down among the non-bid Resources will be as follows:  Renewable, Qualifying Facility, RMR.

(7)	The actual Shift Factors with respect to the Local Congestion of Resources’ individual incremental and decremental prices from above are used to determine the most economical deployment of individual Resources to solve Local Congestion.

(8)	ERCOT will instruct QSEs to deploy Balancing Energy Service from a specific Resource through the issuance of a Dispatch Instruction for each Resource using the most economical solution to resolve the Local Congestion.

(9)	The Dispatch Instruction will specify the instructed output level, the amount of Balancing Energy Service, and the range of acceptable operation of the specific Resource.

(10)	For an incremental Resource-specific instruction, the QSE will be paid in accordance with Section 7.4.3.1, Balancing Energy Up from a Specific Resource.

(11)	For a decremental unit-specific Dispatch Instruction, the QSE will be paid in accordance with Section 7.4.3.2, Balancing Energy Down from a Specific Resource.

(12)	QSEs shall first meet the specific Resource deployment performance requirements of Section 6.10.7, Individual Resource Dispatch Performance and then provide the Balancing Energy Service deployment instructed pursuant to Section 6.7.1, Deployment of Balancing Energy Service.  In the event that a QSE is unable to provide the Balancing Energy Service due to a specific Resource deployment then the QSE will follow the Notification procedures established in Section 5, Dispatch.

(13)	If a Resource is specified as a non-bid Resource, then ERCOT will use OOME to determine the amount paid to the QSE in connection with the Resources dispatched to resolve the constraint.

(14)	The QSEs providing Balancing Energy Service shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Services Deployment Measures.

(15)	ERCOT shall not automatically redeploy nuclear and hydroelectric units using the ERCOT Systems that analyze and resolve transmission Congestion.  ERCOT shall only redeploy nuclear and hydroelectric units manually through the use of a verbal Dispatch Instruction if there is no reasonably practicable Resource solution to Congestion available.

6.7.1.3	Deployment of Balancing Energy During Unusual Events

(1)	During Unusual Events such as major frequency disturbances greater than 0.05 Hz and unexpected significant Load changes greater than half the amount of Regulation Service purchased in either direction, ERCOT may deploy Balancing Energy so as to mitigate the consequences of the Unusual Event.  During such an Event, ERCOT may take one (and only one) the following actions:

(a)	Recall Balancing Energy Up Instruction(s) or a Balancing Energy Down Instruction(s) before the fifteen (15) minute Settlement Interval is complete or without the ten (10) minute notice.  There is no change to the MCPE in the Settlement Interval for this action.  If ERCOT exhausts all recall options, it may deploy unit-specific Balancing Energy based on unit-specific premiums.  The cost of these premiums will be charged to the Balancing Energy Neutrality Adjustment set forth in Section 9.6.1, Balancing Energy Neutrality Adjustment, of these Protocols.

(b)	Deploy Balancing Energy in the same direction as the immediately previous Instruction without the ten (10) minute notice for the remaining of the current Settlement Interval.  For this action, ERCOT must modify the MCPE for the Settlement Interval to the highest price deployed for additional Balancing Energy Up or the lowest price deployed for additional Balancing Energy Down.

6.7.2	Deployment of Regulation Service

(1)	RGS will be deployed in response to a change in ERCOT System frequency to maintain that frequency within predetermined limits.  Deployment will be accomplished through use of an automatic signal from ERCOT to each QSE provider of RGS.

(2)	Dispatch Instructions for regulation capacity will be deployed on a proportional basis, given the ratio of capacity provided, among providers of that capacity having been scheduled for the service.

(3)	ERCOT is required to minimize the use of RGS energy as much as practicable by operating its automatic generation control system in conjunction with deploying Balancing Energy with the objective that Regulation Service Up energy and Regulation Service Down energy are deployed in each Settlement Interval.

(4)	Energy deployed under RGS will not be accounted for separately, but will be settled at the MCPE for Balancing Energy.

(5)	ERCOT shall integrate the control signal sent to providers of Regulation Service Up thus calculating the amount of energy deployed in each Settlement Interval.

(6)	ERCOT shall integrate the control signal sent to providers of Regulation Down Service and calculate the amount of energy deployed in each Settlement Interval.

(7)	ERCOT shall post to all Market Participants the total amount of deployed Regulation Service Up and Regulation Service Down energy in each Settlement Interval of the previous hour.

(8)	QSEs providing Regulation Service shall provide a feedback signal to ERCOT via the MDAS that identifies the amount of regulation energy being provided each control cycle.

(9)	For each QSE providing RGS the implied ramp rate in megawatts per minute is the total amount of Regulation Service awarded divided by ten (10).

(10)	The QSEs providing RGS shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Services Deployment Performance Measures.

6.7.3	Deployment of Responsive Reserve Service

(1)	Responsive Reserve energy shall be deployed as necessary to meet NERC requirements.  This shall be accomplished by:

(a)	Automatic generation action as a result of a significant frequency deviation;

(b)	Through use of an automatic signal and a Dispatch Instruction to deploy Responsive Reserve energy from Generation Resources; and/or

(c)	By Dispatch Instructions for deployment of Responsive Reserve energy from Load acting as a Resource via an electronic Messaging System to providers.

(2)	Deployment of energy as a result of automatic governor action will not be considered as an Uninstructed Deviation.

[PRR307: Revise Section 6.7.3(1) & (2) as follows when system change implemented.] 6.7.3 Deployment of Responsive Reserve Service (1) Responsive Reserve energy shall be deployed as necessary to meet NERC requirements. This shall be accomplished by: (a) Automatic Resource control/governor system action as a result of a significant frequency deviation; (b) Through use of an automatic signal and a Dispatch Instruction to deploy Responsive Reserve energy from Resources; and/or (c) By Dispatch Instructions for deployment of Responsive Reserve energy from Interruptible Load acting as a Resource via an electronic Messaging System to providers. (2) Deployment of energy as a result of automatic Resource control/governor system action will not be considered as an Uninstructed Deviation.

(3)	ERCOT will deploy Responsive Reserve Service in response to disturbance control assistance requirements as specified in the Operating Guides or after all the bids in the Balancing Energy Services Up Bid Stack have been depleted.  Energy from Responsive Reserve Resources will be deployed by ERCOT in accordance with Section 5.6, Emergency and Short Supply Operations.

(4)	ERCOT deployment of Responsive Reserve Service Resources will be proportioned first between suppliers who provide RRS using Generation Resources until thirty-three percent (33%) of the total amount procured by ERCOT is deployed.  If deployment of more than thirty-three percent (33%) is required,  ERCOT shall:

(a)	For frequency restoration caused by an event other than capacity insufficiency, issue an Emergency Notice for frequency restoration and deploy all or a portion of remaining RRS being provided by hydro Resources and by LaaR.

(b)	For frequency restoration related to capacity insufficiency, declare the EECP in effect and follow emergency provisions in Section 5, Dispatch.

(5)	ERCOT will deploy Balancing Energy Service and Non-Spinning Service as soon a practicable to minimize the use of Responsive Reserve energy.

(6)	All providers of Responsive Reserve Resources will be required to provide feedback to ERCOT of their availability and level of deployment in Real Time.  Except in those instances where a significant frequency deviation has occurred and temporary deployment is necessary to meet NERC requirements, ERCOT shall deploy Responsive Reserve Services according to Section 5.6, Emergency and Short Supply Operations.

(7)	Once Responsive Reserve Service is deployed, the Obligation to deliver energy shall remain until specifically instructed by ERCOT to stop providing energy from RRS, but not longer than the period of the service is scheduled.

(8)	The QSEs providing Responsive Reserve Service shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Services Deployment Performance Measures.

[PRR496: Add (9) to Section 6.7.3 as follows when system change implemented.] (9) Responsive Reserve Service procured from a Load Acting as a Resource Block Bid shall be deployed as a block.

6.7.4	Deployment of Non-Spinning Reserve Service

(1)	ERCOT shall deploy Non-Spinning Reserve Service when it predicts more than 95% of the Balancing Energy Service Up available for the Operating Hour will be deployed.

(2)	ERCOT may, in its sole judgment, deploy Non-Spinning Reserve Service as necessary.

(3)	Deployment of Non-Spinning Reserve Service Resources will be proportioned among suppliers.

(4)	NSRS deployment or recall instructions by ERCOT are not constrained by any ramp rate.  However, the QSE is expected to deploy or recall those instructions at a ramp rate that would comply to the instruction in thirty (30) minutes.  During a period of NSRS deployment, all energy provided by the QSE responding to the NSRS deployment will be considered instructed.

(5)	Energy from Non-Spinning Reserve capacity may be deployed in a Congestion Zone by ERCOT if, in its judgment, not enough Balancing Energy Service Up is available to satisfy reliability needs.

(6)	ERCOT will provide Notice via the Messaging System to QSEs of their obligations for NSRS energy as the QSE's Resources are selected.  Providers will be required to respond with manual or electronic acknowledgement.

(7)	All providers of Non-Spinning Reserve Resources will provide Notification to ERCOT of their availability and level of deployment.

(8)	Once deployed, the Obligation to deliver energy will remain until ordered to stop providing by ERCOT (after not less than one hour), but not longer than the period of the service is scheduled.

(9)	NSRS may be deployed at any time in a Settlement Interval.

(10)	The QSEs providing Non-Spinning Reserve Service shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Services Deployment Performance Measures.

[PRR496: Add (11) to Section 6.7.4 as follows when system change implemented.] (11) Non-Spinning Reserve Service procured from a Load Acting as a Resource Block Bid shall be deployed as a block.

6.7.5	Deployment of Replacement Reserve Service

(1)	All units selected to supply this service based on capacity bids will have their Balancing Energy Service bid associated with the service placed in the Balancing Energy Service Bid Stack and will be deployed in accordance with these Protocols.

(2)	Replacement Reserve Service providers are required to provide incremental Balancing Energy Service bids as specified in Section 6.4.2, Determination of ERCOT Control Area Requirements, item (5).  Energy bids from Replacement capacity reserves will be treated as any other incremental energy bid.

(3)	The QSEs providing Replacement Reserve Service shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Services Deployment Performance Measures.

6.7.6	Deployment of Voltage Support Service

(1)	ERCOT, or TSPs designated by ERCOT, will instruct Generation Resources required to provide VSS to make adjustments for voltage support within the URL capacity limits provided by the QSE to ERCOT.  Generation Resources providing VSS will not be requested to reduce megawatt output so as to provide additional megavolt-amperes reactive, nor will they be requested to operate on a voltage schedule outside the Unit Reactive Limits (URL) specified by the QSE without a Dispatch Instruction requesting unit-specific Dispatch or an OOME instruction.

(2)	ERCOT and TDSPs shall develop operating procedures specifying Voltage Profiles of transmission controlled reactive Resources to minimize the dependence on generation-supplied reactive Resources.  For Generation Resources required to provide VSS, step-up transformer tap settings will be managed to maximize the use of the ERCOT System for all Market Participants while maintaining adequate reliability.

(3)	The TSP, under ERCOT direction, is responsible for monitoring and ensuring that all Generation Resources required to provide VSS dynamic reactive sources in a local area are deployed in approximate proportion to their respective installed reactive capability requirements.

(4)	All Generation Resources required to provide VSS shall maintain the transmission voltage at the point of interconnection to the transmission grid as directed by ERCOT within the operating Reactive Power capability of the unit(s).

(5)	At all times a Generation Resource unit required to provide VSS is On-line, the URL must be available for utilization at the generating unit's continuous rated active power output, and Reactive Power up to the unit's operating capability must be available for utilization at lower active power output levels.  In no event shall the Reactive Power available be less than the required installed reactive capability multiplied by the ratio of the lower active power output to the generating unit’s continuous rated active power output, and any Reactive Power available for utilization must be fully deployed to support system voltage upon request by ERCOT, or a TSP.

(6)	The QSEs providing Voltage Support Service shall meet the deployment performance requirements specified in Section 6.10.4, Ancillary Services Deployment Performance Measures.

6.7.7	Deployment of Out-of-Merit Energy Service

Deployment of units for OOME Service will follow Balancing Energy Service deployment guidelines as specified in Section 5, Dispatch.

6.7.7.1	Deployment of Fleet/Zonal OOME

(1)	During circumstances when command and control actions are required, ERCOT may instruct one or more specific QSEs to adjust their total ERCOT generation level or their generation level in a specific Congestion Zone (Zonal) or across all zones (Fleet).  The Dispatch Instruction includes the quantity of energy required and the Congestion Zone(s), if applicable, but does not specify which Generation Resource(s) the QSE(s) should move.  Such a Dispatch Instruction will be referred to as a “Fleet/Zonal OOME Dispatch Instruction.”

(2)	A Fleet/Zonal OOME Dispatch Instruction will be treated as an instructed deviation for Settlement purposes.  When ERCOT issues a Fleet/Zonal OOME Dispatch Instruction, the resulting instructed deviation from the Fleet/Zonal OOME Dispatch Instruction will be defined by the MW amount as specified in the Fleet/Zonal OOME Dispatch Instruction.

(3)	A Fleet/Zonal OOME Dispatch Instruction will be included in the calculation of the SCE.  The Dispatch Instruction will not be constrained by ramp rate; therefore, the change will be considered a step change.

(4)	ERCOT will send Fleet/Zonal OOME Dispatch Instructions to QSEs concurrent with Balancing Energy Service Dispatch Instructions for the target interval.

[PRR 422: Replace (4) above with the following when the system changes are implemented.] (4) For manual deployment of Fleet/Zonal OOME before market clearing, the instructed deviation will be balanced using the Balancing Energy Service Bid Stack. ERCOT will send Fleet/Zonal OOME Dispatch Instructions to QSEs concurrent with Balancing Energy Service Dispatch Instructions for the target interval. The Balancing Energy Service deployment will be limited by the constraints imposed by the Fleet/Zonal OOME Dispatch Instructions. The instructed deviations for these Fleet/Zonal OOME Dispatch Instructions will be included in the Balancing Energy Service Dispatch Instructions for that QSE for the target interval. For the Fleet/Zonal OOME Dispatch Instructions, ERCOT will endeavor to honor the Fleet/Zonal portfolio ramp rate as indicated in the QSE’s Zonal Balancing Energy Service Bids.

6.7.7.2	Deployment of Resource-Specific OOME Before Market Clearing

When ERCOT issues a Resource-specific OOME Dispatch Instruction before the Balancing Energy Service market clears, the instructed deviation resulting from the OOME Dispatch Instruction will be defined as the difference between the instructed output level in the Dispatch Instruction and the Resource Plan output level when the Balancing Energy market clearing engine is initiated for the target service interval except: 1) A Resource is instructed to operate at or above an instructed output level and the planned output level of that Resource is above the instructed output level, or 2) A Resource is instructed to operate at or below an instructed output level and the planned output level of that Resource is below the instructed output level.  The instructed deviation will be balanced using the Balancing Energy Service Bid Stack.  ERCOT will send OOME Dispatch Instructions to QSEs concurrent with Balancing Energy Service Dispatch Instructions for the target interval.  The Balancing Energy Service deployment will be limited by the constraints imposed by the OOME Dispatch Instructions.  The instructed deviations for these OOME Dispatch Instructions will be included in the Balancing Energy Service Dispatch Instructions for that QSE for the target interval.  ERCOT must honor the unit ramp rates set forth in the QSE’s Resource Plan for the applicable Generation Resource.

6.7.7.3	Deployment of OOME After Market Clearing

Resource-specific OOME Dispatch Instructions issued after the Balancing Energy Service market clears will not be instructed deviations.  ERCOT will use its best efforts to minimize Resource-specific OOME and Fleet/Zonal OOME Dispatch Instructions issued after the Balancing Energy Service market has cleared.

6.7.7.4	Out of Merit Energy to Zero (0) MW

When ERCOT issues an OOME Dispatch Instruction to a Resource to operate at a level lower than the Resource’s Low Operating Limit, ERCOT will instruct such Resource down to zero (0) MW for at least the period of the Resource Minimum Down Time.

[PRR454: Replace Section 6.7.7.4 with the following upon system implementation] When ERCOT issues an OOME Dispatch Instruction to a Resource to operate at a level lower than the Resource’s Low Operating Limit, ERCOT will instruct such Resource down to zero (0) MW for at least the period of the Resource Minimum Down Time. The instructed Resource will be paid OOME as well as a single Resource Category Generic Startup Cost if the Resource is recalled and does start during a period it would have been scheduled On-line in its Resource Plan.

6.7.8	Deployment of RMR Service

(1)	If Market Solutions are not available and in Emergency Conditions, ERCOT shall have the option to Dispatch a contracted RMR Unit at any time for voltage support or localized transmission limitations, but it must Dispatch the unit as early as possible (if conditions merit) once conditions are identified that require the use of the RMR Unit and only to the extent of megawatt loading necessary to correct the voltage support or localized transmission limitation.

(2)	ERCOT must elect to use Resources under an RMR Agreement or MRA Agreement before issuing an OOME or Zonal OOME Dispatch Instruction subject to the terms of the Agreement, if practical.

(3)	ERCOT will deploy RMR Units in accordance with the RMR Agreement and MRA Resources in accordance with the MRA Agreement.  RMR Agreements with ERCOT are expected to include limitations on the total service hours, megawatt-hour output, and the number of starts available to ERCOT for each RMR Unit.

(4)	ERCOT shall issue Dispatch Instructions via the Messaging System for any RMR Unit Dispatch or MRA Resource Dispatch.  Any revisions to those instructions must be communicated via revised Dispatch Instructions.

(5)	In the event that ERCOT orders an RMR Unit or MRA Resource to operate to sustain reliable ERCOT System operation in any Operating Day, ERCOT will post on the MIS as soon as possible, but no later than the next Business Day, for such Operating Day:

(a)	each Resource receiving an RMR or MRA Dispatch Instruction for each interval;

(b)	the amount of RMR or MRA energy ERCOT requested from each Resource for each interval; and

[PRR515: Upon system implementation, insert paragraph (c).] (c) the binding transmission constraint (contingency and/or overloaded element(s)) causing RMR or MRA deployments.

(6)	If ERCOT orders an RMR Unit or MRA Resource to operate to sustain reliable ERCOT System operation in any Operating Day, ERCOT will, on or before the Business Day following the day of issuance of the Initial Statement for the Operating Day on which ERCOT issued the Dispatch Instruction, as described in Section 9.2.3, Initial Statements, post on the MIS the amount of RMR or MRA energy actually provided by each RMR or MRA Unit for each interval of the subject Operating Day.

(7)	ERCOT shall publicly post an annual forecast of the Dispatch pattern it expects for each contracted RMR Unit and MRA Resource as well as monthly and week-ahead forecasts regarding its use of such Resources.

(8)	ERCOT will adjust the amount of Balancing Energy acquired due to the impact of RMR Energy deployed and energy deployed from MRA Resources.  If adjustments made by ERCOT would result in the QSE exceeding its scheduled amount of generation, then the affected QSE must not accommodate these changes by adjusting other Resources such that the Schedule Control Error is minimized.  ERCOT will not assess URC charges to the QSE as a result of these adjustments for the interval.  The RMR may implement a Responsibility Transfer between its QSE and ERCOT for energy delivered under an RMR Agreement to minimize the impact of RMR scheduling on its QSE.

6.8	Compensation for Services Provided

This section of the Protocols provides a summary of Ancillary Service payments.

6.8.1	Payments to Providers of Ancillary Services Procured in the Day Ahead and Adjustment Periods

Payments to Providers of Regulation Down, Regulation Up, Responsive Reserves, Non-Spinning Reserves, and Replacement Reserves and Balancing Energy are as described below.

6.8.1.1	Payments for Ancillary Service Capacity

(1)	A QSE whose bid to provide an Ancillary Service Resource to ERCOT is accepted in a particular market in ERCOT’s Day-Ahead and Adjustment Period Ancillary Service procurement process shall be paid for services other than RPRS the amount (in megawatts) of Ancillary Service capacity accepted by ERCOT in that market, multiplied by the MCPC in that market for the Operating Hour.

(2)	During periods of insufficient bids for Ancillary Service markets for RGS, RRS, and NSRS, the following shall apply:

(a)	A QSE whose bid to provide an Ancillary Service Resources has been awarded, shall be paid the amount (in megawatts) of Ancillary Service capacity accepted by ERCOT, multiplied by the MCPC for the Ancillary Service by hour.

(b)	A QSE called upon by ERCOT to provide an Ancillary Service Resource after market insufficiency has been declared, excluding previously accepted bids, shall be paid the amount (in megawatts) of the Ancillary Service capacity called for by ERCOT multiplied by the MCPC that would have resulted if ERCOT had procured only eighty percent (80%) of the capacity procured prior to declaration of insufficiency, for that particular Ancillary Service.

(3)	A QSE whose bid to provide a RPRS Resource to ERCOT is accepted for capacity insufficiency or Zonal Congestion management in ERCOT’s Adjustment Period procurement process shall be paid in accordance with the Zonal Replacement Reserve formula in Section 6.8.1.10, Zonal or System Wide Replacement Reserve Service Capacity Payment to QSE.

(4)	A QSE whose bid to provide a RPRS Resource to ERCOT is accepted for the purpose of Local Congestion management in ERCOT’s Adjustment Period procurement process shall be paid in accordance with the Local Replacement Reserve formula in Section 6.8.1.11, Local Congestion Replacement Reserve Payment to QSE.

6.8.1.2	Regulation Up Service Payment to QSE

A QSE whose bid to provide a Regulation Up Service to ERCOT is accepted in ERCOT’s Ancillary Service procurement process shall be paid for the service as follows:

PCRUqim 	= 	-1 * CRUqim * MCPCRUim

The equation below will be used to determine the Total Regulation Up Service Payment to be allocated to each QSE as described in Section 6.9.1, Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods.

PCRUi	 =	Σ (Σ (PCRUqim)q)m

Where:

i	interval being calculated

m	Procurement for market, m, of the Day Ahead and Adjustment Period

PCRUqim	Regulation Up Payment for that interval Procured Capacity for Regulation Up Reserve Payments ($) for that interval for that QSE determined for market, m.

PCRUi	Procured Regulation Up Capacity Costs ($) for the Total Market for the interval

CRUqim	Awarded Regulation Up Service Capacity (MW) in the market, m, per interval for that QSE

MCPCRUim	The Regulation Up Reserve Market Clearing Price of Capacity Costs ($/MW) per interval of market, m.

6.8.1.3	Emergency Short Supply Regulation Up Capacity Payment to QSE

(1)	Develop a composite Bid Stack containing all bids for Regulation Up Service in the interval.

(2)	Establish the capacity quantity of Megawatts purchased in that interval, in accordance with Section 6.8.1.1, Payments for Ancillary Service Capacity.

(3)	Determine the price as if only eighty percent (80%) of the procured Regulation Up capacity were purchased in that interval.  This becomes the derived price to be used in settlement of Emergency Regulation Up Service, as described below.

(4)	Emergency Short Supply Regulation Up Capacity will be allocated to Load as part of the Regulation Up Load Allocation.

Emergency Short Supply Regulation Up Capacity Payment will be calculated as follows:

PCIESRUqi	=	-1 * (DPRUi * CESRUqi)

The equation below will be used to determine the Total Regulation Up Service Payment to be allocated to each QSE as described in Section 6.9.1, Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods.

PCIESRUi	=  	SUM (PCIESRUqi)q

Where:

i 	interval

PCIESRUqi 	Procured Emergency Capacity Payment for that QSE when insufficient bids for Regulation Up were received for that interval.

PCIESRUi	Emergency Short Supply Regulation Up Capacity Costs ($) for the total Market for the interval

DPRUi	Derived Price ($/MW) of the Ancillary Service that had insufficient bids. (The price, which would have resulted if only eighty percent (80%) of the Regulation Up capacity that was initially bid was awarded).

CESRUi	Regulation Up Capacity (MW) procured from that QSE due to insufficient bids of that service

6.8.1.4	Regulation Down Service Payment to QSE

A QSE whose bid to provide an Regulation Down Service to ERCOT is accepted in ERCOT’s Ancillary Service procurement process shall be paid for the service as follows:

PCRDqim 	= 	-1 * CRDqim * MCPCRDi

The equation below will be used to determine the Total Regulation Down Service Payment to be allocated to each QSE as described in Section 6.9.1, Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods.

PCRDi	 =	SUM (SUM (PCRDqim)q)m

Where:

i:	interval being calculated

m:	Procurement for market, m, of the Day Ahead and Adjustment Period.

PCRDqim:	Regulation Down Payment per interval Procured Capacity for Regulation Down Payments ($) per interval for that QSE determined for market, m.

PCRDi:	Procured Regulation Down Capacity Costs ($) for the Total Market for the interval

CRDqim:	Awarded Regulation Down Service Capacity (MW) in the market, m, per interval for that QSE.

CARDqi 	Awarded Regulation Down Service Capacity (MW) in the Adjustment Market per interval for that QSE

MCPCRDim:	The Regulation Down Service Market Clearing Price of Capacity Costs ($/MW) per interval for market, m.

6.8.1.5	Emergency Short Supply Regulation Down Service Capacity Payment to QSE

(1)	Develop a composite Bid Stack containing all bids for Regulation Down Service in the interval.

(2)	Establish the capacity quantity of Megawatts purchased in that interval, in accordance with Section 6.8.1.1, Payments for Ancillary Service Capacity.

(3)	Determine the price as if only eighty percent (80%) of the procured Regulation Down capacity were purchased in that interval.  This becomes the derived price to be used in settlement of Emergency Short Supply Regulation Down Service, as described below.

(4)	Emergency Short Supply Regulation Down Service Capacity will be allocated to Load as part of the Regulation Down Load Allocation.

Emergency Short Supply Regulation Down Service Capacity Payment will be calculated as follows:

PCIESRDqi	=	-1 * (DPRDi * CESRDqi)

The equation below will be used to determine the Total Regulation Down Service Payment to be allocated to each QSE as described in Section 6.9.1, Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods.

PCIESRDi	=  	Σ (PCIESRDqi)q

Where:

i 	interval

PCIESRDqi 	Procured Emergency Short Supply Service Capacity Payment for that QSE when insufficient bids for Regulation Down were received for that interval.

PCIESRDi:	Emergency Short Supply Service Regulation Down Capacity Costs ($) for the total Market for the interval

DPRDi	Derived Price ($/MW) of the Ancillary Service had insufficient bids, (the price which would have resulted if only eighty percent (80%) of the Regulation Down capacity that was initially supplied was awarded).

CESRDqi	Emergency Short Supply Regulation Down Service Capacity (MW) from that QSE procured due to insufficient bids of that service

6.8.1.6	Responsive Reserve Service Payment to QSE

A QSE whose bid to provide an Responsive Reserve Service to ERCOT is accepted in ERCOT’s Ancillary Service procurement process shall be paid for the service as follows:

PCRRqim 	= 	-1 * CRRqim * MCPCRRim

The equation below will be used to determine the Total Responsive Reserve Service Payment to be allocated to each QSE as described in Section 6.9.1, Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods.

PCRRi	= 	SUM (SUM (PCRRqim)q)m

Where:

i	interval being calculated

m	Procurement for market, m, of the Day Ahead and Adjustment Period.

PCRRqim	Responsive Reserve Service Payment per interval Procured Capacity for Responsive Reserve Payments ($) per interval for that QSE determined for market, m.

PCRRi	Procured Responsive Reserve Capacity Costs ($) for the Total Market for the interval

CRRqim	Awarded Responsive Reserve Service Capacity (MW) in the market, m, per interval for that QSE

MCPCRRi	Responsive Reserve Market Clearing Price of Capacity Costs ($/MW) per interval for market, m.

6.8.1.7	Emergency Short Supply Responsive Reserve Service Capacity Payment to QSE

(1)	Develop a composite Bid Stack containing all bids for Responsive Reserve Service in the interval.

(2)	Establish the capacity quantity of Megawatts purchased in that interval, in accordance with Section 6.8.1.1, Payments for Ancillary Service Capacity.

(3)	Determine the price as if only eighty percent (80%) of the procured Responsive Reserve capacity were purchased in that interval.  This becomes the derived price to be used in settlement of Emergency Responsive Reserve Service, as described below.

(4)	Emergency Short Supply Responsive Reserve Service Capacity will be allocated to Load as part of the Responsive Reserve Load Allocation.

Emergency Short Supply Responsive Reserve Service Capacity Payment will be calculated as follows:

PCIESRRqi	=	-1 * (DPRRi * CESRRqi)

The equation below will be used to determine the Total Responsive Reserve Service Payment to be allocated to each QSE as described in Section 6.9.1, Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods.

PCIESRRi	=  	SUM(PCIESRRqi)q

Where:

i 	interval

PCIESRRqi 	Procured Emergency Service Responsive Reserve Capacity Payment for each QSE when insufficient bids for Responsive Reserve were received in that interval.

PCIESRRi	Emergency Short Supply Responsive Reserve Capacity Costs ($) for the total Market for the interval

DPRRi	Derived Price ($/MW) of the Ancillary Service that had insufficient bids, (the price which would have resulted if only eighty percent (80%) of the Responsive Reserve capacity that was initially bid was awarded).

CESRRqi	Emergency Short Supply Responsive Reserve Capacity (MW) from that QSE procured due to insufficient bids of that service

6.8.1.8	Non-Spinning Reserve Service Payment to QSE

A QSE whose bid to provide an Non-Spinning Reserve Service to ERCOT is accepted in ERCOT’s Ancillary Service procurement process shall be paid for the service as follows:

PCNSqim 	= 	-1 * CNSqim * MCPCNSim

The equation below will be used to determine the Total Non-Spinning Reserve Service Payment to be allocated to each QSE as described in Section 6.9.1, Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods.

PCNSi	=	SUM (SUM (PCNSqim)q)m

Where:

i:	interval being calculated

m:	Procurement for market, m, of the Day Ahead and Adjustment Period.

PCNSqim:	Procured Capacity for Non-Spinning Reserve Payments ($) for that interval for that QSE determined for market, m.

PCNSi:	Procured Non-Spinning Reserve Capacity Costs ($) for the Total Market for the interval

CNSqim:	Awarded Non-Spinning Reserve Service Capacity Quantity (MW) in the market, m, per interval for that QSE Service

MCPCNSim:	Non-Spinning Reserve Service Market Clearing Price of Capacity Costs ($/MW) per interval of market, m.

6.8.1.9	Emergency Short Supply Non-Spinning Reserve Service Capacity Payment to QSE

(1)	Develop a composite Bid Stack containing all bids for Non-Spinning Reserve Service in the interval.

(2)	Establish the capacity quantity of Megawatts purchased in that interval, in accordance with Section 6.8.1.1, Payments for Ancillary Service Capacity.

(3)	Determine the price as if only eighty percent (80%) of the procured Non-Spinning Reserve capacity were purchased in that interval.  This becomes the derived price to be used in settlement of Emergency Non-Spinning Reserve Service, as described below.

(4)	Emergency Short Supply Non-Spinning Reserve Service Capacity will be allocated to Load as part of the Non-Spinning Reserve Load Allocation.

Emergency Short Supply Non-Spinning Reserve Service Capacity will be calculated as follows:

PCIESNSqi	=	-1 * (DPNSi * CESNSqi)

The equation below will be used to determine the Total Non-Spinning Reserve Service Payment to be allocated to each QSE as described in Section 6.9.1, Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods.

PCIESNSi	=	SUM (PCIESNSqi)q

Where:

i	interval

PCIESNSqi	Procured Emergency Short Supply Service Non-Spinning Capacity Payment for that QSE when insufficient bids for Non-Spinning were received in that interval.

PCIESNSi	Emergency Short Supply Service Non-Spinning Capacity Costs ($) for the total Market for the interval

DPNSi	Derived Price ($/MW) of the service when the Ancillary Service that had insufficient bids. (The price, which would have resulted if only eighty percent (80%) of the Non-Spinning capacity bids that were initially bid, were awarded).

CESNSqi	Non-Spinning Capacity (MW) from that QSE procured due to insufficient bids of that service

6.8.1.10	Zonal or System Wide Replacement Reserve Service Capacity Payment to QSE

A QSE whose unit bid to provide RPRS to ERCOT is accepted in ERCOT’s Ancillary Service procurement process shall be paid for services in the amount (in MW) of RPRS capacity accepted by ERCOT, multiplied by the maximum of the bid price or the highest MCPC of that interval per zone of all the RPRS procurement processes for a single Operating Hour, excluding any RPRS procured to resolve Local Congestion and is paid as follows:

PCRPqi 	= 	 SUM (PCRPqiuz)u

Given:

PCRPqiuz 	= 	-1 * Max(PABCRPiu, MCPCRPiz )* ZCRPqiuz

PABCRPiu	=	CBPRPiu/N + HOBPRPiu

Where:

i	interval being calculated

z	zone

u	single Resource

N	Number of hours that this Resource is continuously procured

CBPRPiu	Capacity bid price submitted by the QSE for the single Resource

HOBPRPiu	Hourly operational bid price submitted by the QSE for the single Resource

MCPCRPiz	Highest Replacement Reserve Service Market Clearing Price of all procurement processes of Capacity ($/MW) per interval per zone, excluding any RPRS procured to resolve Local Congestion

PABCRPiu	Bid Price of the single Resource awarded Replacement Reserve in that interval

PCRPqiuz	Replacement Reserve Service Payments ($) by Resource per interval for that QSE

PCRPqi	Replacement Reserve Payments ($) Service Payment per interval for that QSE

ZCRPqiuz	Accepted Unit Adjustment Replacement Reserve Service Capacity Quantity (MW) to solve insufficiency or Zonal Congestion per interval per zone per QSE per single Resource.

The equation below will be used to determine the Total Replacement Reserve Payment to be allocated to each QSE as described in Section 6.9.2, QSE Obligations for Capacity Services Procured in the Day Ahead and Adjustment Periods.

PCRPi 		= 	SUM (PCRPqi)q

Where:

i 	interval being calculated

q	QSE

PCRPqi	Replacement Reserve Payments ($) Service Payment per interval for that QSE

PCRPi	Summation of Replacement Reserve Payments ($) per interval for all QSEs in the market

6.8.1.11	Local Congestion Replacement Reserve Payment to QSE When a Market Solution Exists

(1)	The QSE for a Resource selected to provide RPRS to resolve Local Congestion that actually reconnects to the ERCOT Transmission Grid and starts the unit in order to provide RPRS will be paid both the Resource Category Generic Startup Cost for starting the unit and the Resource Category Generic Minimum Energy Cost less the MCPE for operating at the Low Sustainable Limit (LSL) as set forth in the Resource Plan for that unit during the instructed interval(s).  If the MCPE during the intervals of an hour in which ERCOT deploys a Resource for RPRS provides revenue in excess of the hourly cost to start and operate the unit at LSL, the QSE representing the Resource may retain any such excess revenue.

(2)	Resources that are connected to the ERCOT Transmission Grid when the QSE is instructed to provide RPRS to resolve Local Congestion will be paid the Resource Category Generic Minimum Energy Cost less the MCPE for operating at the Low Sustainable Limit of the Resource during the instructed interval(s).

(3)	If ERCOT instructs a QSE to provide RPRS from a Resource to resolve Local Congestion and the payment for RPRS does not cover the cost of providing the RPRS plus a ten percent (10%) premium, then that QSE will be paid all approved, verifiable, incremental costs (“Additional Costs”) exceeding the payment for RPRS.  The QSE will be paid only for Additional Costs directly attributable to the RPRS instruction, plus the premium.  The Additional Costs shall be limited to:

(i)	Fuel (including the cost of exceeding swing gas contract limits, additional gas demand costs set by fuel supply, or transportation contracts);

(ii)	Fuel transportation;

(iii)	Maintenance;

(iv)	Chemicals; and

(v)	Water.

The premium shall be ten percent (10%).  The Resource Entity for the Resource that received the RPRS Instruction shall submit to ERCOT supporting data for the Additional Costs.  The QSE that received the RPRS instruction shall be bound by the supporting data submitted by the Resource Entity.  The Resource Entity must submit the support data to ERCOT as soon as reasonably possible, but in no event less than thirty (30) days before the date set forth in the ERCOT Settlement Calendar for the issuance of a True-Up Statement for the subject Operating Day.  QSEs requesting Additional Costs shall do the following:

(a)	After receiving the Initial Settlement Statement for the subject Operating Day, submit a settlement dispute in accordance with the dispute process outlined in Section 9.5, Settlement Billing and Dispute Process.  In addition to the standard information required on the dispute form on the ERCOT Portal, the dispute should clearly indicate:

(i)	The Dispatch Instruction received from ERCOT to provide the RPRS;

(ii)	The payment received for providing the RPRS;

(iii)	The actual cost of providing the RPRS; and

(iv)	A reference to the documentation to be provided in writing as indicated in these Protocols.

(b)	Provide written documentation to allow ERCOT to verify the claimed amounts.  Documentation requirements for each cost type are as follows:

(i)	Fuel cost for providing the RPRS shall be determined by taking the product of the fuel consumption (MMBtu) at the Low Operating Limit of the Resource and its associated fuel cost ($/MMBtu);

(ii)	Fuel consumption at the Low Operating Limit shall be based upon a heat rate curve for the Resource from the most recently conducted heat rate tests.  Test data shall be provided in sufficient detail to allow for the validation of the heat rate curve provided;

(iii)	Fuel costs, including transportation costs, will require supporting documentation of sufficient detail to allow for the verification of the cost of fuel consumed at the deployed Resource.  Documentation may include contracts, invoices, or other documents all of which will be treated as Protected Information pursuant to Section 1.3.1.1, Items Considered Protected Information, item (11).  All copies of such documentation will be returned upon completion of the review on request by the QSE or the Resource Entity.  For gas fired Resources, such documentation will not be required if the requested incremental fuel cost is less than one hundred fifteen percent (115%) of the Fuel Index Price;

(iv)	Maintenance costs shall be calculated based on actual maintenance contracts, prorated accordingly; and

(v)	Chemical and water costs shall be calculated based on actual contracts, prorated accordingly.

(4)	The calculation for RPRS to resolve Local Congestion is as follows:

LPCRPiuq	=	-1 *	MAX( 0, LPSRPiu + LPORPiu )

LPCRPiq	= 	SUM (LPCRPiuq)u

LPORPiu	=	SUM[(RCGMECc-MCPEjz) * MIN(MINCAPiu/4,MRju)]j

If the unit is deemed to be Off-line as described in Section 6.8.1.11 item (1)

Then:

LPSRPiu	 =	RCGSCc/N

If the unit is deemed to be On-line as described in Section 6.8.1.11 item (2)

Then:

LPSRPiu	=	0

The equation below will be used to determine the Total Replacement Reserve Payment to be allocated to each QSE as described in Section 6.9.2, QSE Obligations for Capacity Services Procured in the Day Ahead and Adjustment Periods.

LPCRPi	=	SUM (LPCRPiq)q

Where:

c	Resource Category

i	Hourly interval being calculated

j	Settlement Intervals within the hourly interval i

u	Resource

q	QSE

z	Zone

N	Number of hours that this Resource is continuously procured

LPCRPiuq	Replacement Reserve Service payment ($) per interval for the Resource

LPCRPiq	Replacement Reserve Service payments ($) per interval for that QSE

LPCRPi	Summations of Replacement Reserve Service payments ($) to resolve Local Congestion per interval for all QSEs

LPSRPiu	Price for starting a unit that is selected for Replacement Reserve Service to resolve Local Congestion

LPORPiu	Price for operating a unit that is selected for Replacement Reserve Service to resolve Local Congestion

MINCAPiu	Generating Unit Low Sustainable Limit as reported in the unit’s Resource Plan

MRju	Actual metered output of the Resource

RCGMECc	Resource Category Generic Minimum Energy Cost for a specific category of generation unit

RCGSCc	Resource Category Generic Startup Cost for a specific category of generation unit

[PRR454: Add Section 6.8.2.6 upon system implementation:] 6.8.2.6 Payment When a Resource Receives an OOME Down to Zero (0) MW Dispatch Instruction (1) Resources that are issued Dispatch Instructions to provide OOME Down Service to zero (0) MW, and which actually shut down to follow such Dispatch Instructions, will be paid both the OOME Cost defined in Section 6.8.2.3, Energy Payments, for the instructed interval(s) and Resource Category Generic Capacity Startup Cost for each instructed shut down. (2) Compensation for additional types of cost, not outlined above, must be reviewed and approved by the ERCOT Board of Directors during an Executive Session of its next regularly scheduled meeting. Requests must be presented in person by a representative of the company submitting the request and must also include language suitable to be included in the Protocols to define the documentation requirements for future requests of a similar nature. Subsequent to the approval of such costs, the requesting company shall submit a Protocol Revision Request, in accordance with Section 21, Process for Protocol Revision, incorporating the necessary documentation standards provided to the ERCOT Board. (3) The calculation of startup payment for the Resource that receives an OOME Down Dispatch Instruction to provide service to zero (0) MW is: PSu = RCGSCc Where: PSu Startup payment for the Resource which receives an OOME Down Dispatch Instruction to zero (0) MW c Resource Category u Single Resource RCGSCc Resource Category Generic Startup Cost for a specific category of generation unit

6.8.1.12	Payments for Balancing Energy Provided from Ancillary Services During the Operating Period

All Balancing Energy deployed by a Dispatch Instruction and delivered by a generating Resource from Balancing Energy Service, Responsive Reserve Service, Regulation Reserve Service, or Non-Spinning Reserve Service shall be settled as Balancing Energy at the MCPE of the Congestion Zone of the Resource providing the energy according to Section 6.8.1.13, Resource Imbalance.  All Balancing Energy deployed by a Dispatch Instruction and delivered by a Load acting as Balancing Energy Service, Responsive Reserve Service, Regulation Reserve Service, or Non-Spinning Reserve Service shall be settled as Balancing Energy at the MCPE of the Congestion Zone of the Resource providing the energy according to Section 6.9.5.2, Settlement for Balancing Energy for Load Imbalance.  Settlement for any energy provided without an authorized Dispatch Instruction will be settled according to Section 6.8.1.15, Payments for Balancing Energy Provided from Uninstructed Deviation.

Deployed Balancing Energy Up on qualified Balancing Up Loads will be paid a capacity payment for the first Settlement Interval that it is deployed equal to the MCPC of Non-Spinning Reserve Service for the hour in which the deployment occurs.  A continuous deployment of Balancing Energy Up on qualified Loads for over sixty (60) minutes will be paid a capacity payment for each subsequent Settlement Interval which it is deployed equal to the MCPC of Non-Spinning Reserve Service for that hour divided by four (4).

6.8.1.13	Resource Imbalance

Resource Imbalance ($) for each QSE for each interval for each zone will equal the Resource schedule (MWh) for Resources represented by that QSE minus the actual meter read (MWh) for the Resource multiplied by the Market Clearing Price for Energy ($/MWh).  Resource Imbalance does not exclude DC Ties.

All generating Resource Balancing Energy deployed by a Dispatch Instruction from Balancing Energy Service, Responsive Reserve Service, Regulation Reserve Service, or Non-Spinning Reserve Service shall be paid as follows:

RIiq 	= 	SUM (RIizq)z

Given:

RIizq 	=	NTEizq * MCPEiz

NTEizq	=	(QRSizq  - MRizq)

The equation below represents the total Resource Imbalance Charges in a Congestion Zone for each interval.

RIiz 	= SUM (RIizq)q

Where:

i:	interval being calculated

z:	zone being settled

q	QSE

RIizq	Resource Imbalance ($) per interval per zone by QSE

RIiq	Resource Imbalance ($) per interval for that QSE

RIiz	Summation of Resource Imbalance ($) payments per interval per zonal for all QSEs in the market

NTEizq	Net Energy per interval per zone per QSE is the difference between Resources scheduled and metered value

MRizq	Metered value (MWh) for the Resource per interval, per zone per QSE using actual and/or estimated values

QRSizq	Resource schedule (MWh) per interval per zone per QSE.

MCPEiz	Market Clearing Price of Energy ($/MWh) per interval per zone

6.8.1.14	Payments for Capacity for Balancing Energy Up Load Deployed

A QSE that is instructed to deploy Balancing Up Load (BUL) shall be paid a capacity payment for the 15-minute interval the instruction is issued and the three (3) subsequent intervals according to the following formulas.  A QSE that is instructed to continue to deploy BUL after the first four (4) 15-minute intervals will be paid a capacity payment for each subsequent interval instruction it is given to deploy BUL.  The BUL capacity payment is calculated as follows:

PCBULiq	=	-1 *(( MBULiq * MCPCNSi )/ 4)

MBULiq	=	MAX(BULiq-0, BULiq-1, BULiq-2, BULiq-3)

BULPMiq	=	BULETRiq –all…zone(BMRDiq + BMRSiq)

BULETRiq	=	[((BRATDiq * AIMLDiq) + (BRATSiq * AIMLSiq)) – ((∑FSBULizq)z + (∑DSBULizq)z)]

[PIP112, PRR311, & PRR448: Insert the following when BUL Small Customer Load Management is implemented:] Given: IF Small Customer Load Management THEN BULiq = AIMLLMiq – BMRLMiq ELSE:

BULiq	=	MIN[MIN(MAX(0,(∑DIBULizq)z), MAX(0,((BRATDiq*AIMLDiq)-BMRDiq))) + MAX(0,((BRATSiq*AIMLSiq)-BMRSiq)), (∑DQiqz)z]

DIBULizq	=	MAX[0, (∑(MRizq – 	(DSLizq + INSizq + INSewiq + SRSizq))z)]

AIMLDiq=n=1xBMRDqin−MAXn=1,...,xBMRDqi1,⋯,BMRDqix−MINn=1,...,xBMRDqi1,⋯,BMRDqixx−2

AIMLSiq=n=1xBMRSqin−MAXn=1,...,xBMRSqi1,⋯,BMRSqix−MINn=1,...,xBMRSqi1,⋯,BMRSqixx−2

AMLPDiqn=BMRDqi−8n8

AMLPSiqn=BMRSqi−8n8

AMLPBDiq=n=1xAMLPDiqnx−2

AMLPBSiq=n=1xAMLPSiqnx−2

BRATDiq=AMLPDiq0AMLPBDiq

BRATSiq=AMLPSiq0AMLPBSiq

Where:

i	Settlement Interval being calculated

q	QSE

x	count of proxy days

z	zone

AIMLDiq	Representative average interval metered BUL during the last ten (10) proxy days (in the case of weekdays) or six (6) proxy days (if deployment is on a weekend or holiday) for BUL meters that represent dynamic Load.  Proxy days cannot be days when BUL was deployed during any interval.

[PIP112, PRR311, & PRR448: Insert the following when BUL Small Customer Load Management is implemented:] AIMLLMiq QSE aggregate baseline Load for small customers who participate in Load management program assuming the program is not in operation from the appropriate Load Profile.

AIMLSiq	Representative average interval metered BUL during the last ten (10) proxy days (in the case of weekdays) or six (6) proxy days (if deployment is on a weekend or holiday) for BUL meters that represent static Load.  Proxy days cannot be days when BUL was deployed during any interval.

AMLPBDiq	Average interval metered BUL from the prior ten (10) proxy days (in the case of weekday deployment) or six (6) proxy days (for weekend or holiday deployment) for the two (2) hours prior to first BUL instruction for BUL meters that represent dynamic Load.  Proxy days cannot be days when BUL was deployed during any interval.

AMLPBSiq	Average interval metered BUL from the prior ten (10) proxy days (in the case of weekday deployment) or six (6) proxy days (for weekend or holiday deployment) for the two (2) hours prior to first BUL instruction for BUL meters that represent static Load.  Proxy days cannot be days when BUL was deployed during any interval.

AMLPDiqn	Average interval metered BUL during the two (2) hours prior to the hour of BUL Notice in the nth prior day for BUL meters that represent dynamic Load.  Note, that n=0 refers to day of notice.

AMLPSiqn	Average interval metered BUL during the two (2) hours prior to the hour of BUL Notice in the nth prior day for BUL meters that represent static Load.  Note, that n=0 refers to day of notice.

BMRDiq	Aggregate of all actual qualified BUL meter readings per QSE per Settlement Interval per zone for BUL meters that represent dynamic Load.

BMRDqimn	Aggregate of all qualified dynamic BUL meter readings per QSE q during the mth 15-minute time interval after the Settlement Interval i on the nth day prior to the day of settlement, where the n prior days shall be only weekdays excluding ERCOT-defined holidays if the day of settlement is a weekday, and shall be only weekends and ERCOT-defined holidays if the day of settlement is a weekend.  Days in which BUL instructions occurred are excluded.

[PIP112, PRR311, & PRR448: Insert the following when BUL Small Customer Load Management is implemented:] BMRLMiq QSE aggregate participating Customer Load during operation of Load management program from the appropriate Load Profile.

BMRSiq	Aggregate of all actual qualified BUL meter readings per QSE per Settlement Interval per zone for BUL meters that represent static Load.

BMRSqimn	Aggregate of all qualified static BUL meter readings per QSE q during the mth 15-minute time interval after the Settlement Interval i on the nth day prior to the day of settlement, where the n prior days shall be only weekdays excluding ERCOT-defined holidays if the day of settlement is a weekday, and shall be only weekends and ERCOT-defined holidays if the day of settlement is a weekend.  Days in which BUL instructions occurred are excluded.

BRATDiq	Ratio of average metered dynamic Load for 2 hours prior to BUL instruction to the average interval metered BUL from the prior ten (10) days (in the case of weekday deployment) or six (6) days (for weekend or holiday deployment) for the two (2) hours prior to first BUL instruction.

BRATSiq	Ratio of average metered static load for two (2) hours prior to BUL instruction to the average interval metered BUL from the prior ten (10) days (in the case of weekday deployment) or six (6) days (for weekend or holiday deployment) for the two (2) hours prior to first BUL instruction.

BULiq	Quantity in MWhs of BUL deployed per Settlement Interval per QSE.

BULETRiq	Total BUL expected reduction by QSE per interval ERCOT-wide.

BULPMiq	Calculated to determine whether a QSE performed the BUL deployment and should receive a capacity payment.

DIBULizq	For QSEs with Dynamically Scheduled Loads, the average power delivered to ERCOT per interval per zone as a result of deploying BUL.

DQiqz	Deployed  BUL quantity in MW per zone.

DSBULizq	For QSEs with Dynamically Scheduled Loads, the integrated signal for the interval that is an estimate in Real Time representing the real power interrupted in response to the deployment of BUL.  DSBULizq = zero (0) if Load is not dynamically scheduled.

DSLizq	The integral of the Dynamically Scheduled Load telemetered to ERCOT for that QSE per interval per zone.

FSBULizq	Integrated signal for the interval sent by static scheduling QSEs to ERCOT and is an estimate in Real Time representing the real power interrupted in response to the deployment of BUL.

INSewiq	ERCOT-wide instructions for that QSE per interval.

INSizq	Zonal Balancing Energy instructions given to that QSE per zone per interval.

MBULiq	Maximum quantity in MWhs of BUL deployed per Settlement Interval per QSE.

MCPCNSi	Highest Non-Spinning Reserve Service Market Clearing Price of Capacity costs ($/MW) for the hour of all procurement processes.

MRizq	Metered Resource value for that QSE per interval per zone.

PCBULiq	Capacity payment for instructed deployment of BUL per Settlement Interval per QSE.

SRSizq	Static Resource schedule per interval per zone of that QSE.

6.8.1.15	Payments for Balancing Energy Provided from Uninstructed Deviation

Resources will be paid the full Market Clearing Price for Energy for up to the amount of all ERCOT instructed schedule deviations on an ERCOT-wide basis.

Resources will be paid a fraction of the market-clearing price for Uninstructed Deviations on an ERCOT-wide basis.  An Uninstructed Deviation has occurred whenever the total metered Resources of a QSE for a Settlement Interval are different from the total of the scheduled Resources plus any Resource deployments instructed by ERCOT.  An Uninstructed Deviation for a QSE will be equal to the energy that results during a Settlement Interval from the integrated schedule plus Dispatch Instructions minus the sum of the net metered value for the Generation Resources plus Load Resource response to Dispatch Instructions as described in Section 6.10.4, Ancillary Service Deployment Performance Measures.

6.8.1.15.1	Uninstructed Resource Charge Process

Once ERCOT has determined the Congestion Zones in which the Uninstructed Deviations of the QSE have occurred, an uninstructed pricing differential will be applied to a QSE representing Resources whenever one of the following two (2) conditions exists:

(1)	The QSE representing Resources has total metered Resources for any Settlement Interval that are greater than the larger of one hundred one and one-half percent (101.5%) of the QSE’s total of schedules plus instructions or five (5) MWh over the total of schedules plus instructions when the integrated amount of ERCOT-wide regulation is less than negative twenty-five (– 25) MWhs in the interval.  Upon one-day Notice, ERCOT can reduce the percentage and MWh tolerance to one hundred one percent (101%) and three (3) MWh, respectively, if significant price chasing exists.

(2)	The QSE representing Resources has total metered Resources for any Settlement Interval that are less than the lesser of ninety-eight and one-half percent (98.5%) of the total schedule plus instructions or five (5) MWh under the total of schedules plus instructions when the integrated amount of ERCOT-wide regulation is greater than positive twenty-five (+ 25) MWh in the interval.  Upon one day Notice, ERCOT can increase the percentage and MWh tolerance to ninety-nine percent (99%) and three (3) MWh, respectively, if significant price chasing exists.

(3)	A QSE that schedules Uncontrollable Renewable Resources will not be subject to Uninstructed Deviation Pricing for the Uncontrollable Renewable Resources to the extent that the total metered Uncontrollable Renewable Resource does not exceed one hundred fifty percent (150%) or is not less than fifty percent (50%) of its schedule in any schedule interval.  The Renewable Production Potential of such Uncontrollable Renewable Resource may be used in lieu of its schedule for the purpose of determining whether the Uncontrollable Renewable Resource is subject to URC if the Resource Entity also makes an irrevocable commitment to use such Renewable Production Potential for all OOME Down payments in lieu of the Resource Plan output level. The terms of this Protocol Section 6.8.1.15.1 shall immediately apply to QSEs that only represent Uncontrollable Renewable Resources, and to all QSEs at such time that ERCOT can account for different Resource types in the Scheduling Process and can allocate Regulation Service requirements among Loads and Uncontrollable Renewable Resources electing to utilize Renewable Production Potential for URC and OOME according to their Energy Ratio Share.

If any condition listed in items (1) or (2), above, exists, then an Uninstructed Deviation pricing differential will be applied as follows:

(a)	QSEs would be paid (or pay) for Instructed and Uninstructed Deviations at the zonal MCPE under Resource Imbalance Charge.

(b)	An Uninstructed Deviation Charge Back would be calculated at a factor of the MCPE.  The Uninstructed Deviation Charge Back would be applied to each Congestion Zone that a QSE has a deviation from schedule.

When the two conditions described in items (1) and (2), above, are met, an Uninstructed Factor will be instituted to reduce the payment to the QSE.  The Uninstructed Factor will be adjusted in relation to the amount of Regulation Reserve Service that was required during that interval on a sliding scale.

Once a regulation is determined to be over or under the defined bandwidth, a QSE would be subject to the uninstructed charge for over-generation when the MCPE is positive, and for under-generation when the MCPE price is negative.

6.8.1.15.2	Determining the Uninstructed Factor

The Uninstructed Factor is a factor used to reduce the total payments made to a Resource for Uninstructed Deviations.  The Uninstructed Factor could change by interval, depending on the following three conditions:

(1)	The ERCOT approved MWh range of tolerance for regulation deployment in a Settlement Interval;

(2)	The system wide integral amount above the tolerance level for Regulation Reserve Services (variable by interval);

(3)	The upper limit of the amount (MWh) in which the Regulation Reserve Services can be deployed before the factor maximizes.  The upper limit will be set at 125 MWh.

From a programmatic perspective, the Uninstructed Factor would be determined in the following manner:

WITHIN TOLERANCE: when regulation is deployed within the pre-defined tolerance level, the Resource receives one hundred percent (100%) of its Balancing Energy payment;

IF  Eregup < tolerance AND Eregdown < tolerance THEN

UFi	=	0

CASE OVERGENERATION: when regulation down is deployed beyond the pre-defined tolerance level, a QSE will be charged back for generation over their aggregated schedules and instructions;

ELSE IF Eregdown > tolerance THEN

UFi	=	min(1.0, Eregdown,i−tolerance

CASE UNDERGENERATION: when regulation up is deployed beyond the tolerance level and any MCPEz is negative a QSE will be charged back for generation under their aggregated schedules and instructions as above.

ELSE Eregup > tolerance

UFi	=	min(1.0, Eregup,i−tolerance

Graphically, if the tolerance were +/- 25 MWhs of regulation, the Uninstructed Factor would look like this:

6.8.1.15.3	Uninstructed Charge Methodology and Equation

Once the Uninstructed Factor is determined on a system-wide basis for the Settlement Interval, it is possible to determine the ‘price’ to apply to QSE uninstructions.  The Uninstructed Resource Charge would be determined by QSE for each zone in which the QSE had actual metered Resources.

The first step is to determine the QSE’s Total Uninstructed Deviation.  Each QSE’s Total Uninstructed Deviation is calculated by adding the QSE Resource Schedule and all zonal and ERCOT wide instructions, and subtracting that amount from the Metered Resource Value.  A dead band will be set according to each QSE’s schedule plus instructions.  If the QSE’s Metered Resource Value is within this dead band percentage of  +/- 1.5% but not less than +/-5 MWh of the Schedule plus instructions for a Settlement Interval, then the QSE will not be subject to the Uninstructed Resource Charge.

[PIP112: Although the formula did not change, the “BUL” language incorporates Load Resources into one of the variables (MR). The current design does not have that capability. Once reworked, the following words in this comment box could be added to the protocols.] The QSE’s Metered Resource Value will include both Generation and Load Resources. The amount of energy provided by a Load Resource will be obtained from the information submitted on the Resource Plan and the Settlement Meter of the Load Resource. Energy from a Load Resource is calculated for each Load Resource that is indicated available on the Resource Plan according to the following formula: Energy from Load Resource = MAX (0, MIN ((the integral of the upper operating limit –Load Settlement Meter), (integral of the upper operating limit - integral of the lower operating limit))) At the request of the QSE as specified by Section 6.10.6, ERCOT will disregard energy from a Load Resource for the four consecutive Settlement Intervals following the time of the request by the QSE as it relates to the following formula.

TUDiq=All zoneMRizq−SRURCizq+INSizq+ DSBULizq−INSewiq

Where:

TUDiq	Total ERCOT-wide Uninstructed Deviation for that QSE per Settlement Interval

MRizq	Metered Resource Value for that QSE per Settlement Interval per zone

SRURCizq	The Resource Schedule (with out any DC Tie import schedules) smoothed for a 10-minute ramp per Settlement Interval per zone of that QSE, plus the Dynamic Schedule per Settlement Interval per zone of that QSE, plus the DC Tie import schedules per Settlement Interval per zone of that QSE.

INSizq	Zonal Balancing Energy instructions given to that QSE per zone per Settlement Interval

INSewiq	ERCOT-wide Instructions for that QSE per Settlement Interval

DSBULizq	For QSEs with Dynamically Scheduled Loads, the integrated signal for the Settlement Interval that is an estimate in Real Time representing the real power interrupted in response to the deployment of BUL.  DSBULizq = zero (0) if Load is not dynamically scheduled.

If the QSE’s Total Uninstructed Deviation is zero, then the zonal Uninstructed Deviation for every zone is zero.

ZUDizq = 0

If the QSE’s Total Uninstructed Deviation is positive, then the total Uninstructed Deviation will be allocated to those zones in which the value of adding the QSE’s Resource Schedule in that zone and zonal instructions in that zone, and subtracting from the Metered Resource Value in that zone is positive.

ZUDizq=max(0,MRizq−(SRURCizq+INSizq+DSBULizq))all  zonemax(0,MRizq−(SRURCizq+INSizq+DSBULizq))∗TUDiq

If the QSE’s Total Uninstructed Deviation is negative, then the total Uninstructed Deviation will be allocated to those zones in which the value of adding the QSE’s Resource Schedule in that zone and zonal instructions in that zone, and subtracting from the Metered Resource Value in that zone is negative.

ZUDizq=min(0,MRizq−(SRURCizq+INSizq+DSBULizq))all  zonemin(0,MRizq−(SRURCizq+INSizq+DSBULizq))∗TUDiq

Where:

i	interval

q	QSE

z	Congestion Zone

INSizq	Zonal Balancing Energy instructions given to that QSE per zone per interval.

MRizq	Metered Resource Value for that QSE per interval per zone.

SRURCizq	=	SRSURCizq + (SRAizq or SRDizq) + DC Tie import schedulesizq

SRSURCizq	=	SRSNDCCURRizq + ((SRSNDCPREVizq - SRSNDCCURRizq) / 12)+((SRSNDCNEXTizq - SRSNDCCURRizq) / 12)

[PRR601: replace the equation above with the following upon system implementation:] SRSURCizq = SRSNDCCURRizq + ((SRSNDCPREVizq - SRSNDCCURRizq) / 8)+((SRSNDCNEXTizq - SRSNDCCURRizq) / 8)

Where:

INSizq	Zonal Balancing Energy instructions given to that QSE per zone per interval.

MRizq	Metered Resource Value for that QSE per interval per zone.

SRURCizq  =  SRSURCizq + (SRAizq or SRDizq) + DC Tie import schedulesizq

SRSURCizq = SRSNDCCURRizq + ((SRSNDCPREVizq - SRSNDCCURRizq) / 12)+((SRSNDCNEXTizq - SRSNDCCURRizq) / 12)

[PRR601: replace the equation above with the following upon system implementation:] SRSURCizq = SRSNDCCURRizq + ((SRSNDCPREVizq - SRSNDCCURRizq) / 8)+((SRSNDCNEXTizq - SRSNDCCURRizq) / 8)

Where:

DC Tie import schedulesizq	The DC Tie imports scheduled per interval per zone of that QSE.

(SRAizq or SRDizq)	The scheduled Resource (actual or dynamic, which ever is selected based on the dynamic scheduling logic) per interval per zone of that QSE.

SRSNDCCURRizq	The scheduled Resource static minus any DC Tie import schedules, for the current interval, per interval per zone per QSE.

SRSNDCNEXTizq	The scheduled Resource static minus any DC Tie import schedules for the next interval, per interval per zone per QSE.

SRSNDCPREVizq	The scheduled Resource static minus any DC Tie import schedules for the previous interval, per interval, per zone, and per QSE.

SRSURCizq	The scheduled Resource static (without any DC Tie import schedules) smoothed for a ten (10) minute ramp, per interval per zone of that QSE.

[PRR601: replace the definition above with the following upon system implementation:] SRSURCizq The scheduled Resource static (without any DC Tie import schedules) smoothed for a fifteen (15) minute ramp, per interval per zone of that QSE.

SRURCRSizq	The Resource Schedule (without any DC Tie import schedules) smoothed for a ten (10) minute ramp per interval per zone of that QSE, plus the Dynamic Schedule per interval per zone of that QSE, plus the DC Tie import schedules per interval per zone of that QSE.

[PRR601: replace the definition above with the following upon system implementation:] SRURCRSizq The Resource Schedule (without any DC Tie import schedules) smoothed for a fifteen (15) minute ramp per interval per zone of that QSE, plus the Dynamic Schedule per interval per zone of that QSE, plus the DC Tie import schedules per interval per zone of that QSE.

TUDiq	Total ERCOT wide Uninstructed Deviation for that QSE per interval.

ZUDizq	Zonal Uninstructed Deviation for that QSE per interval for that zone.

DSBULizq	For QSEs with Dynamically Scheduled Loads, the integrated signal for the interval that is an estimate in Real Time representing the real power interrupted in response to the deployment of BUL.  DSBULizq = zero (0) if Load is not dynamically scheduled.

The second step is to compare the market-clearing price of an interval to a benchmark in each zone and calculate the Uninstructed Resource Charge for each QSE in each zone.  If the MCPE for the zone is negative, a QSE would be subject to the Uninstructed Resource Charge for under-generation.  If the MCPE is positive, then a QSE is subject to the Uninstructed Resource Charge for over-generation.

The Uninstructed Resource Charge for that zone will be the product of the zonal uninstructed quantity, the MCPE for that Settlement Interval for that zone, and the previously determined Uninstructed Factor for that Settlement Interval.

This activity would be performed for every Congestion Zone for each QSE.

CASE: PRICE CHASING

IF MCPEiz  0 and QSE outside deadband, then:

URCizq=Max0,ZUDizq∗MCPEiz×UFi

CASE: COST OPTIMIZING

ELSE MCPEiz < 0 and QSE outside deadband Then:

URCizq=Min0,ZUDizq∗MCPEiz×UFi

Where:

URCiz	Uninstructed Resource Charge for that QSE per zone per Settlement Interval

ZUDizq	Zonal Uninstructed Deviation for that QSE per zone per Settlement Interval

MCPEiz	Market Clearing Price for Energy in that zone of that Settlement Interval

UFi	Uninstructed Factor determined in accordance to deployed regulation

6.8.2	Capacity and Energy Payments for Out-of-Merit or Zonal OOME Service

6.8.2.1	Resource Category Generic Costs

To properly calculate Local Congestion costs, it is necessary to establish certain generic costs associated with Resources that will be used to calculate production costs incurred when the Resource(s) provides Out of Merit or Zonal OOME Service.  These generic Resource costs include generic fuel costs and generic startup costs.

(1)	Each ERCOT Generation Resource will be assigned to one of the following Resource Categories for the purpose of determining generic fuel costs:

Nuclear

Hydro

Coal and Lignite

Combined Cycle greater than 90 MW**

Combined Cycle less than or equal to 90 MW**

Gas-Steam Supercritical Boiler

Gas-Steam Reheat Boiler

Gas-Steam Non-reheat or boiler without air-preheater

Simple Cycle greater than 90 MW

Simple Cycle less than or equal to 90 MW

Diesel (and all other diesel or gas-fired Resources)

Renewable (i.e., non-Hydro renewable Resources)

Block Load Transfer

[PRR543: Add the following upon ERCOT Legal review of the Comision Federal de Electricidad contract:] BtB Tie with non-ERCOT Control Area

**	Determined by capacity of largest simple cycle combustion turbine in the train

The category of each Resource will be reported to ERCOT by the Generation Entity.  Each Generation Entity shall ensure that each of its Resources is in the correct Resource category.

(2)	The Fuel Index Price (FIP) shall be the Midpoint price, expressed in $/MMBtu, published in Gas Daily, in the Daily Price Survey, under the heading “East-Houston-Katy, Houston Ship Channel” for the day of the OOMC or OOME deployment.  The FIP for Saturdays, Sundays, holidays and other days for which there is no FIP published in Gas Daily, shall be the next published FIP after the day of the OOMC or OOME deployment.  In the event that the FIP is not published for more than two (2) days, the previous day published FIP will be used for Initial Settlement and the next day published FIP will be used for the Final Settlement Statement.

(3)	Resource Category Generic Fuel Costs

Each ERCOT Generation Resource will be assigned a Resource Category Generic Fuel Cost (RCGFC) based on the Resource Category to which it is assigned.  For Nuclear, Hydro, Coal and Lignite Resources, the RCGFC will be a fixed dollar/MWh amount as shown below.  For the remaining Resource categories (except Renewable), the RCGFC will be the product of a heat rate (based on the heat rates used for the Capacity Auction) and a Fuel Index Price (FIP).  The RCGFC for Renewable Resources will be $0/MWh.

The RCGFC for each type of Resource for upward instructions will be:

Nuclear = $15.00/MWh

Hydro = $10.00/MWh

Coal and Lignite = $18.00/MWh

Combined Cycle greater than 90 MW** = FIP * 9 MMBtu/MWh

Combined Cycle less than or equal to 90 MW** = FIP * 10 MMBtu/MWh

Gas-Steam Supercritical Boiler = FIP * 10.5 MMBtu/MWh

Gas-Steam Reheat Boiler = FIP * 11.5 MMBtu/MWh

Gas-Steam Non-reheat or boiler without air-preheater = FIP * 14.5 MMBtu/MWh

Simple Cycle greater than 90 MW = FIP * 14 MMBtu/MWh

Simple Cycle less than or equal to 90 MW = FIP * 15 MMBtu/MWh

Diesel = FIP * 16 MMBtu/MWh

Block Load Transfer = FIP * 18 MMBtu/MWh

[PRR543: Add the following upon ERCOT Legal review of the Comision Federal de Electricidad contract:] Back to Back Tie with non-ERCOT Control Area = FIP * 18 MMBtu/MWh

Renewable = $0/MWh

LaaR = FIP * 18 MMBtu/MWh

**	Determined by capacity of largest simple cycle combustion turbine in the train

The RCGFC for each type of Resource for downward instructions will be:

Nuclear = $0.00/MWh

Hydro = $0.00/MWh

Coal and Lignite = $3.00/MWh

Combined Cycle greater than 90 MW** = FIP * 5 MMBtu/MWh

Combined Cycle less than or equal to 90 MW** = FIP * 6.5 MMBtu/MWh

Gas-Steam Supercritical Boiler = FIP * 7.5 MMBtu/MWh

Gas-Steam Reheat Boiler = FIP * 9.5 MMBtu/MWh

Gas-Steam Non-reheat or boiler without air-preheater = FIP * 10.5 MMBtu/MWh

Simple Cycle greater than 90 MW = FIP * 10.5 MMBtu/MWh

Simple Cycle less than or equal to 90 MW = FIP * 12 MMBtu/MWh

Diesel = FIP * 12 MMBtu/MWh

Block Load Transfer = Not Applicable

[PRR543: Add the following upon ERCOT Legal review of the Comision Federal de Electricidad contract:] BtB Tie with non-ERCOT Control Area = Not Applicable

Renewable = $0/MWh

**	Determined by capacity of largest simple cycle combustion turbine in the train

(4)	Resource Category Generic Startup Costs

Resource Category Generic Startup Costs (RCGSC) represents the startup cost of capacity used for Replacement Reserve Service.  The RCGSC for each type of Resource will be:

Nuclear = $0.00/MWh

Hydro = $0.00/MWh

Coal and Lignite = $0.00/MWh

Combined Cycle – when there are five hours or more between shutdown and startup for an OOMC instruction:

Combined Cycle greater than 90 MW** = $6,810 + (FIP * 2,200 MMBtu)

Combined Cycle less than or equal to 90 MW** = $5,310 + (FIP * 1,200 MMBtu)

Combined Cycle – when there are less than five (5) hours between shutdown and startup for an OOMC instruction:

Combined Cycle greater than 90 MW** = $6,810 + (FIP * 1,100 MMBtu)

Combined Cycle less than or equal to 90 MW** = $5,310 + (FIP * 600 MMBtu)

Gas-Steam Supercritical Boiler = $4,800 + (FIP * 16.5 MMBtu/MW * RMCu)

Gas-Steam Reheat Boiler = $3,000 + (FIP * 9.0 MMBtu/MW * RMCu)

Gas-Steam Non-reheat or boiler without air-preheater = $2,310 + (FIP * 2.30 MMBtu/MW * RMCu)

Simple Cycle greater than 90 MW = $5,000 + (FIP * 1.1 MMBtu/MW * RMCu)

Simple Cycle less than or equal to 90 MW = $2,300 + (FIP * 1.1 MMBtu/MW * RMCu)

Renewable = $0

Where:

RMC	Resource Maximum Capacity (in MW)

u	unit

**	Determined by capacity of largest Simple Cycle combustion turbine in the train

(5)	Resource Category Generic Minimum Energy Cost

Resource Category Generic Minimum Energy Cost (RCGMEC) is the heat rate of a unit, in one of these categories, at its Low Sustainable Limit as set forth in the Resource Plan for that unit (as required by Section 4.4.15, QSE Resource Plans) when the Resource is selected to provide Out-of-Merit Service multiplied by the Fuel Index Price as defined in Section 6.8.2.1, Resource Category Generic Costs, item (2).  The RCGMEC for each type of Resource will be:

Nuclear Units  = zonal MCPE for the units location

Hydro Units  = zonal MCPE for the units location

Coal & Lignite Units  = zonal MCPE for the units location

Combined Cycle greater than 90 MW** = 10 MMBtu/MWh * FIP

Combined Cycle less than or equal to 90 MW** = 10 MMBtu/MWh * FIP

Gas-Steam Supercritical Boiler = 16.5 MMBtu/MWh * FIP

Gas-Steam Reheat Boiler = 17.0 MMBtu/MWh * FIP

Gas-Steam Non-reheat or boiler without air-preheater = 19.0 MMBtu/MWh * FIP

Simple Cycle greater than 90 MW = 15.0 MMBtu/MWh * FIP

Simple Cycle less than or equal to 90 MW = 15.0 MMBtu/MWh * FIP

**	Determined by capacity of largest simple cycle combustion turbine in the train

6.8.2.2	Capacity and Minimum Energy Payments

(1)	OOMC Service may be used by ERCOT as a procured Replacement Reserve Resource in the Adjustment Period where necessary to support emergency operations and provide voltage support, stability, or to manage localized transmission limitations.  All Generation Resources that are available and plan to be off-line during the interval for which Ancillary Services are being procured are eligible to be selected to provide OOMC Service.  ERCOT shall not issue an OOME Up Dispatch Instruction for the energy associated with the Low Sustainable Limit as set forth in the Resource Plan (as required by Section 4.4.15, QSE Resource Plans) for which it has issued an OOMC Dispatch Instruction.  Zonal OOME Service will only be provided from Resources that are already On-line at the time of the Zonal OOME Dispatch Instruction and will not receive a capacity payment.

(2)	The QSE for a Generation Resource selected to provide OOMC Service that actually reconnects to the ERCOT Transmission Grid and starts the unit in order to provide the OOMC Service will be paid both the Resource Category Generic Startup Cost for starting the unit as well as the Resource Category Generic Minimum Energy Cost less the MCPE for operating at the Low Sustainable Limit as set forth in the Resource Plan for that unit during the instructed interval(s).

(3)	If the Generation Resource remains On-line beyond the time period specified by the OOMC Dispatch Instruction, there shall be a charge against the Resource Category Generic Startup Cost.  This charge will only be applied if the MCPE is greater than the Resource Category Generic Fuel Cost for an upward instruction.  If the difference is positive and the Resource Category Generic Startup Cost due is greater than zero, it will be subtracted from the payment for Resource Category Generic Startup Cost for starting the unit.  This charge shall continue to be calculated for all intervals, except for the first three hours after the end of the OOMC Dispatch Instruction, until:

(a)	the unit is disconnected from the ERCOT Transmission Grid;

(b)	the end of the Operating Day; or

(c)	the next Resource-specific deployment for the unit within the Operating Day, whichever comes first.

(4)	Generation Resources that are connected to the ERCOT Transmission Grid when their QSE is instructed to provide OOMC Service will be paid the Resource Category Generic Minimum Energy Cost less the MCPE for operating at the Low Sustainable Limit of the Resource during the instructed interval(s).

When the Resource-specific OOMC instruction is issued, the QSE may maintain a Balanced Schedule, such as scheduling the ramping and minimum energy or being selected by ERCOT to provide Balancing Energy Service.  When a QSE receives an OOMC Dispatch Instruction less than thirty minutes before the end of the Adjustment Period or during the Operating Period, the deviation resulting from ramping or minimum energy of a Resource selected to provide OOMC Service will not be subject to Uninstructed Resource Charge during the instructed interval(s), including the ramp interval(s) of such Resource.

(5)	If ERCOT sends a QSE a Resource-specific Dispatch Instruction for OOMC Service (“OOMC Instruction”) and the payment for OOMC Service does not cover all costs of providing the OOMC Service plus a ten percent (10%) premium, then that QSE may submit verifiable, additional costs directly attributable to the OOMC Dispatch Instruction, which exceed the payment for OOMC Service calculated pursuant to Section 6.8.2.2 (6).  The QSE will be paid only for additional costs directly attributable to the OOMC Service, plus the premium. Verifiable costs are subject to the approved documentation requirements in Section 6.8.2.2(5)(b).  The premium to be provided shall be the product of the costs of providing the service times ten percent (10%).  Verification of these costs must be submitted to ERCOT by the QSE or the Resource to allow resolution by the end of the dispute process for Settlement True-Up as defined in Section 9.2.6, True-Up Statement.  QSEs requesting cost based recovery shall perform the following:

(a)	After receiving the Initial Statement for the subject Operating Day, submit a settlement dispute in accordance with the dispute process outlined in Section 9.5, Settlement and Billing Dispute Process.  In addition to the standard information required on the dispute form on the ERCOT Portal, the dispute should clearly indicate:

(i)	The Dispatch Instruction received from ERCOT to provide the OOMC Services;

(ii)	The payment received for providing the OOMC Service;

(iii)	The actual cost of providing the OOMC Service; and

(iv)	A reference to the documentation to be provided in writing as indicated in Section 6.8.2.2(5)(b).

(b)	Provide documentation to allow ERCOT to verify the claimed amounts.  All documentation submitted to ERCOT for verification pursuant to this Section 6.8.2.2(5)(b) shall be considered Protected Information in accordance with Section 1.3.1.1, Items Considered Protected Information.  ERCOT shall not make payments for verifiable costs outside the defined documentation requirements until after the QSE has followed the steps outlined in Section 6.8.2.2(5)(c) and the ERCOT Board has approved the documentation requirements.  Fuel costs, including transportation and storage costs directly related to this OOMC event for use in calculating the costs in Section 6.8.2.2(5)(b) (i), (iii) and (v), will require supporting documentation of sufficient detail to allow for the verification of the cost of fuel consumed by the Resource receiving the OOMC Instruction.  Documentation may include contracts, invoices or other documents.  For gas fired Resources, such documentation will not be required if the requested incremental fuel cost is less than one hundred ten percent (110%) of the Fuel Index Price.

Defined Documentation Requirements

(i)	Startup Fuel Cost which is the fuel cost for bringing the unit online and up to its LSL and ready to go to full load or the beginning of the OOMC period, whichever occurs first, to provide the OOMC Service shall be determined by multiplying the fuel consumption (MMBtu) to start up the Resource by the associated fuel cost ($/MMBtu).

(ii)	Startup Non-Fuel Cost which shall be based on either A or B below:

(A)	Documented historical non-fuel startup costs expressed on a per unit start basis for the deployed Resource.  If the historical Non-Fuel Startup costs are more than one hundred percent (100%) of the Resource Category Non-Fuel Startup Costs (RCNFSC), the QSE shall provide documentation for such costs. Non-fuel start-up costs are limited to the costs associated with water, chemicals, labor, emission allowances and start-up power used in the start-up of the Resource. Supporting documentation shall include an itemized list in sufficient detail to allow for the verification of each cost incurred due to the OOMC Service.

(B)	Generic Resource Category Non-Fuel Startup Costs (RCNFSC) as defined in Section 6.8.2.2(5)(b)(ii)(B).  If the QSE chooses to use RCNFSC, all subsequent requests for non-fuel startup cost-based recovery requested by the QSE for the remainder of the calendar year for the specific deployed Resource shall be based on the RCNFSC.

Resource Category Non-Fuel Startup Costs (RCNFSC)

For the purpose of documentation, the RCNFSC represents the startup cost (excluding fuel) of capacity used for Replacement Reserve Service.  The RCNFSC for each type of Resource shall be:

Combined Cycle greater than 90 MW** = $6,810

Combined Cycle less than or equal to 90 MW** = $5,310

Gas-Steam Supercritical Boiler = $4,800

Gas-Steam Reheat Boiler = $3,000

Gas-Steam Non-reheat or boiler without air-preheater = $2,310

Simple Cycle greater than 90 MW = $5,000

Simple Cycle less than or equal to 90 MW = $2,300

Renewable = $0

**	Determined by capacity of largest simple-cycle combustion turbine in the train

(iii)	Operational Fuel Cost, which shall be determined by multiplying the fuel consumption (MMBtu) at the Low Sustainable Limit of the Resource by its associated fuel cost ($/MMBtu) for the intervals covered by the OOMC Instruction.  Fuel consumption at the Low Sustainable Limit shall be based upon a heat rate curve for the Resource from the most recently conducted heat rate tests filed with ERCOT.  Test data shall be provided in sufficient detail to allow ERCOT to validate the heat rate curve provided.

(iv)	Variable non-fuel maintenance cost (in dollars per MWh) for a specific deployed Resource, which shall be calculated based on: actual itemized variable maintenance costs contained in contracts with a third party or the manufacturer’s recommended maintenance schedule and associated costs.  Supporting documentation will be the corresponding excerpt of the appropriate contract from the third party or the maintenance schedule.

(v)	Fuel cost for bringing the unit offline from LSL as soon as possible (not to exceed three (3) hours) after the end of the OOMC period, in a manner consistent with Good Utility Practices, shall be determined by multiplying the fuel consumption (MMBtu) to bring the Resource offline by the associated fuel cost ($/MMBtu) minus the MCPE multiplied by the actual generation for shut down.  Fuel quantity will be based on the Real-Time metering of the fuel consumption for the Resource.

(vi)	Unavoidable costs directly resulting from a delay in an accepted Outage for a Generating Resource due to an OOMC instruction.  Supporting documentation shall include an itemized list in sufficient detail to allow for the verification of each cost incurred due to the Outage delay.  Further documentation supporting each line item must be provided upon ERCOT’s request and may include copies of contracts, vendor invoices or other documents.

(c)	Compensation for types of cost, whose documentation requirements are not covered in Sections 6.8.2.2(5)(b)(i) through 6.8.2.2(5)(b)(vi) for the deployed Resource, will be denied pending possible review by the ERCOT Board of Directors.  The requesting QSE may request approval of the documentation requirements by the Board, and if requested will be considered by the Board at its next regularly scheduled meeting for which proper notice may be posted following ERCOT’s receipt of the request.  The requesting party may request that this review be conducted at an Executive Session of the ERCOT Board of Directors. Requests must be presented in person by a representative of the company submitting the request and must also include language suitable to be included in the Protocols to define the documentation requirements for future requests of a similar nature.  Subsequent to the approval of such costs, the requesting company shall submit a Protocol Revision Request, in accordance with Section 21, Process for Protocol Revision, incorporating the necessary documentation standards provided to the ERCOT Board.  Once approved by the ERCOT Board, ERCOT will process the request for payments as described in Section 9.2.5, Resettlement Statement.

(d)	Submit a signature sheet signed by the authorized representative of the Resource Entity certifying the costs submitted are directly attributable to the OOMC deployment and which satisfies the documentation standards in Section 6.8.2.2(5)(b).

(6)	The calculation for capacity payments and minimum energy of Out of Merit Service is as follows:

PCOOMRPqi	=	SUM (PCOOMRPqui)u

If BPRPqui exists,

Then:

PCOOMRPqui	=	-1* MIN [(BPRPqui * COOMRPui),  (PSui + POui)]

Else:

PCOOMRPqui	=	-1 * (PSui + POui)

If the unit is deemed to be On-line as described in 6.8.2.2(4),

Then:

PSui	=	0

POui	=	SUM [(RCGMECc – MCPEjz) * MIN (MINCAPu/4, MRuj)]j

If the unit is deemed to be Off-line as described in 6.8.2.2(2),

Then:

PSui	=	[RCGSCc – (SUMs(MCPEwz * MRuw))] / (# of instructed hours)

POui	=	SUM [(RCGMECc – MCPEjz) * MIN (MINCAPu/4, MRuj)]j

If the unit is not a Nuclear, Hydro, Coal or Lignite unit and continues to remain On-line after the instructed intervals as described in 6.8.2.2(3),

Then:

CRCGSC	=	SUMa [(MCPEaz – RCGFCc) * MRua]

If CRCGSC	>	0 and [RCGSCc – SUMs(MCPEwz * MRuw)] > 0

Then:

PSui	=	Max(0, {RCGSCc – SUMs(MCPEwz * MRuw)-CRCGSC} / (# of instructed hours))

POui	=	SUM [(RCGMECc – MCPEjz) * MIN (MINCAPu/4, MRuj)]j

If CRCGSC 	≤	0

Then:

PSui 	=	{[RCGSCc – (SUMs(MCPEwz * MRuw))] / (# of instructed hours)}

POui	=	SUM [(RCGMECc – MCPEjz) * MIN (MINCAPu/4, MRuj)]j

The equation below will be used to determine the Total OOM Capacity Payments to be allocated to each QSE as described in Section 6.9.7.1, OOM Capacity Charge.

PCOOMRPi	=	SUM (PCOOMRPqi)q

Where:

a	Settlement Intervals beginning three (3) hours after the end of an OOMC Dispatch Instruction and continuing until the unit goes Off-line, the end of the Operating Day, or the next Resource-specific deployment, whichever occurs first

c	Resource Category

i	hourly interval

j	Settlement Intervals within the hourly interval, i

q	QSE

s	The twelve (12) Settlement Intervals prior to the Dispatch Instruction

u	single Resource

w	Settlement Interval prior to the Dispatch Instruction

z	zone

BPRPqui	Bid Price for Replacement Reserve ($/MW) of the unit per interval

COOMRPui 	Out of Merit Replacement Reserve Capacity awarded capacity (MW) per single Resource per interval

CRCGSC	Charge against the Resource Category Generic Startup Cost due if the generation unit continues to run past a Dispatch Instruction.

MCPEaz	Market Clearing Price for Energy during a Settlement Interval between the end of a Dispatch Instruction and the unit going Off-line, the end of the Operating Day, or the next OOMC deployment, whichever occurs first

MCPEjz	Market Clearing Price for Energy during a Settlement Interval within the hourly interval, i

MCPEwz	Market Clearing Price for Energy for a Settlement Interval prior to the Dispatch Instruction

MINCAPu	Generating unit Low Sustainable Limit as reported in the Resource Plan

MRua	Actual metered output of the Resource during a Settlement Interval between the end of a Dispatch Instruction and the unit going Off-line, the end of the Operating Day, or the next OOMC deployment, whichever occurs first

MRuj	Actual metered output of the Resource during a Settlement Interval within the hourly interval, i

MRuw	Actual metered output of the Resource for a Settlement Interval prior to the Dispatch Instruction

PCOOMRPi	Summation of OOM Replacement Capacity Payment ($) per interval for all QSEs in the market

PCOOMRPqi	Total OOM Replacement Reserve Capacity Payment ($) by interval for that QSE (All OOM single Resources added together for that QSE)

PCOOMRPqui 	OOM Replacement Reserve Capacity Payments by single Resource by interval for that QSE

POui	Price for operating a unit that is selected Out of Merit Order to provide Balancing Energy.

PSui	Price for starting a unit that is selected Out of Merit Order to provide Balancing Energy.

RCGFCc	Resource Category Generic Fuel Cost for a specific category for upward instructions.

RCGMECc	Resource Category Generic Minimum Energy Cost for a specific category of generation unit

RCGSCc	Resource Category Generic Startup Cost for a specific category of generation unit

6.8.2.3	Energy Payments

(1)	Whenever a Generation Resource is called for OOME Up or Zonal OOME Up, the QSE will receive any Resource Imbalance payment it is entitled to receive as specified in Section 6.8.1.13, Resource Imbalance.  In addition, an OOME payment adjustment will be made such that the resulting total payment to the Resource(s) is equal to the higher of either: (a) Resource Category Generic Fuel Cost (RCGFC) for the Resource(s); or the (b) MCPE for the Congestion Zone.

(2)	The calculation for Generation Resources OOME Up or Zonal OOME Up is as follows:

PEOOMUPiq 	=	SUM (PEOOMUPiuq)uq+ SUM (PEOOMUPivq)vq

Where:

PEOOMUPiuq	=	-1 * EOOMUPiuq * Max [(RCGFCc - MCPEiz), 0]

EOOMUPiuq	=	Max (0, Min ((MRiuq - OLiuq), IOOMUPiuq))

PEOOMUPivq	=	-1 * EOOMUPivq * Max [(RCGFCc - MCPEiz), 0]

EOOMUPivq	=	Max (0, Min ((MRivq – OLivq), NETUEQivq)) * OOMAGRivq

The equation below will be used to determine the Total OOM Energy Payments to be allocated to each QSE in Section 6.9.7.2, OOM Energy Charge.

PEOOMUPi 	=	SUM (PEOOMUPiu)  + SUM (PEOOMUPiv)

NETUEQivq	=	Max(0,((NETOOMUEQivq + NETLBEUQivq) – (NETOOMDEQivq + NETLBEDQivq))

NETOOMUEQivq 	=	Max(0, (SUM(IOOMUPqui)u – SUM(IOOMDNqui)u))

NETLBEUQivq 	=	Max(0, (SUM(LBEUQqui)u – SUM(LBEDQqui)u))

NETOOMDEQivq	=	Max(0, (SUM(IOOMDNqui)u – SUM(IOOMUPqui)u))

NETLBEDQivq 	=	Max(0, (SUM(LBEDQqui)u – SUM(LBEUQqui)u))

OOMAGRivq	=	[SUM(IOOMUPqui)u + SUM(IOOMDNqui)u] / [SUM(LBEUQqui)u + SUM(LBEDQqui)u + 
SUM(IOOMUPqui)u + SUM(IOOMDNqui)u]

Where:

c	Resource category

i	interval

u	individual generation unit (including units within an Aggregated Unit)

v	Aggregated Unit

z	zone

q	QSE

MCPEiz	Market Clearing Price of Energy for that interval of the zone in which unit resides

PEOOMUPiuq	Out of Merit Energy Up Payment ($) for that interval per unit per QSE

PEOOMUPivq	Out of Merit Energy Up Payment ($) for that interval per Aggregated Unit per QSE

PEOOMUPiq	Out of Merit Energy Up Payment ($) for that interval per QSE

PEOOMUPi	Summation of Out of Merit Energy Up Payment ($) per interval for all QSEs in the market

EOOMUPiuq	OOM Up quantity deployed for that unit per interval per QSE

EOOMUPivq	OOM Up quantity deployed for that Aggregated Unit per interval per QSE

IOOMUPiuq	OOM Energy Up Instructions for that interval for that unit converted to MWh for that interval by dividing by the interval count per hour (4 per hour for 15 minute Settlement Interval)

IOOMDNiuq	OOM Energy Down Instructions for that interval for that unit converted to MWh for that interval by dividing by the interval count per hour (4 per hour for 15 minute Settlement Interval)

MRiuq	Meter Reading for that unit for that interval per QSE

MRivq	Meter Reading for that Aggregated Unit for that interval per QSE.

OLiuq	Resource Plan output level submitted by the QSE for the specific unit given the OOM instruction for that interval.

OLivq	Resource Plan output level submitted by the QSE for the Aggregated Unit containing the specific unit given the OOM instruction for that interval.

RCGFCc	Resource Category Generic Fuel Cost for a specific category.

NETOOMUEQivq The net of all unit-specific OOM instructions (Up minus Down) that result in a positive value.

NETLBEUQivq	The net of all unit-specific Local Balancing Energy Instructions (Up minus Down) that result in a positive value.

NETOOMDEQivq The net of all unit-specific OOM instructions (Down minus Up) that result in a positive value.

NETLBEDQivq The net of all unit-specific Local Balancing Energy Instructions (Down minus Up) that result in a positive value.

LBEUQqui	Local Balancing Energy Up Instructions for that interval per specific unit

LBEDQqui	Local Balancing Energy Down Instructions for that interval per specific unit

NETUEQiv	The overall net direction per the instructions given to the Aggregated Unit results in an up direction

OOMAGRiv 	The percentage of the aggregated instructions to the Aggregated Unit that represents the OOM Energy market.

(3)	If ERCOT sends a Resource-specific Dispatch Instruction for OOME Up or Zonal OOME Up Service and the payment for OOME Service does not cover all costs of providing the Service, then that QSE may submit verifiable, additional costs directly attributable to the OOME Dispatch Instruction, which exceed the payment for OOME Service calculated pursuant to Section 6.8.2.3(2).  Verifiable costs are subject to the approved documentation requirements in Section 6.8.2.3(4)(b).  These costs may include the cost of exceeding swing gas contract limits, additional gas Demand costs set by the fuel supply or transportation contracts, and any additional costs to purchase emissions credits or other costs incurred due to environmental regulations.  Verification of these costs must be submitted to ERCOT by the QSE or the Resource to allow resolution by the end of the dispute process for Settlement True-Up as defined in Section 9.2.6, True-Up Statement.

(4)	If a QSE requests cost-based recovery, the entire payment will be based solely on verifiable costs.  QSEs requesting such cost recovery shall perform the following:

(a)	After receiving the Initial Settlement Statement for the subject Operating Day, submit a settlement dispute in accordance with the dispute process outlined in Section 9.5, Settlement and Billing Dispute Process.  In addition to the standard information required on the dispute form on the ERCOT Portal, the dispute should clearly indicate:

(i)	The Dispatch Instruction received from ERCOT to provide the OOME Services;

(ii)	The payment received for providing the OOME Service;

(iii)	The actual cost of providing the OOME Service;

(iv)	A reference to the documentation to be provided in writing as indicated in these Protocols; and

(b)	Provide written documentation to allow ERCOT to verify the claimed amounts.  All documentation submitted to ERCOT for verification pursuant to this Section 6.8.2.3(4)(b) shall be considered Protected Information in accordance with Section 1.3.1.1, Items Considered Protected Information.

ERCOT shall not make payments for verifiable cost outside the defined documentation requirements until after the QSE has followed the steps outlined in Section 6.8.2.3(4)(b) and the ERCOT Board has approved the documentation requirements.

Fuel costs, including transportation and storage costs, will require supporting documentation of sufficient detail to allow for the verification of the cost of fuel consumed at the deployed Resource.  Documentation may include contracts, invoices or other documents.  For gas fired Resources, such documentation will not be required if the requested incremental fuel cost is less than one hundred ten percent (110%) of the Fuel Index Price.

Defined Documentation Requirements

(i)	Operational Fuel Cost for providing the OOME Service shall be determined by multiplying the change in instructed energy (MWh) due to the OOME instruction by the associated Marginal Heat Rate (MMBtu/MWh) and the associated fuel cost ($/MMBtu) of the instructed Resource for the intervals that the Resource was procured to provide the OOME Service.

(ii)	The Marginal Heat Rate shall be determined by subtracting the total amount of fuel burn of the Resource (in MMBtu/hr) based on the planned output shown in the Resource Plan from the total amount of fuel burn (in MMBtu/hr) based on the lesser of the instructed level of the Resource or the actual Resource output, dividing the result by the net change in output level from the Resource Plan to the lesser of the instructed level of the Resource or the actual output of the unit (in MW).  The amount of fuel consumed (in MMBtu) to provide OOME Service shall be calculated from the input/output curve coefficients or linear interpolation of test data points for the Resource from the most recently conducted heat rate tests filed with ERCOT.  Test data shall be provided in sufficient detail to allow for the validation of the heat rate curve provided.

(c)	Compensation for types of cost, whose documentation requirements are not covered in Sections 6.8.2.3(4)(b)(i) through 6.8.2.3(4)(b)(ii) for the deployed Resource, will be denied pending possible review by the ERCOT Board of Directors.  The requesting QSE may request approval of the documentation requirements by the Board, and if requested will be considered by the Board at its next regularly scheduled meeting for which proper notice may be posted following ERCOT’s receipt of the request.  The requesting party may request that this review be conducted at an Executive Session of the ERCOT Board of Directors.  Requests must be presented in person by a representative of the company submitting the request and must also include language suitable to be included in the Protocols to define the documentation requirements for future requests of a similar nature.  Subsequent to the approval of such costs, the requesting company shall submit a Protocol Revision Request, in accordance with Section 21, Process for Protocol Revision, incorporating the necessary documentation standards provided to the ERCOT Board.  Once approved by the ERCOT Board, ERCOT will process the request for payments as described in Section 9.2.5, Resettlement Statement.

(d)	Submit a signature sheet signed by the authorized representative of the Resource Entity certifying the costs submitted are directly attributable to the OOME deployment and which satisfies the documentation standards in Section 6.8.2.3(4)(b).

(5)	Whenever a Generation Resource is called on for OOME Down or Zonal OOME Down, the QSE will be paid an energy payment equal to the total amount of energy to be reduced by the Resource, multiplied by the greater of: (a) the difference between (i) the MCPE of the Congestion Zone and (ii) the RCFGC for that Resource or (b) $0.00.  The calculation for OOME Down is as follows:

PEOOMDNiuqz	=	-1 * EOOMDNiu  * Max (0,(MCPEiz-RCGFCc))

EOOMDNiu 	= 	Max (0, Min((OLuiq - MRiu ),IOOMDNiuq))

PEOOMDNivqz	=	-1 * EOOMDNiv  * Max (0,(MCPEiz-RCGFCc))

EOOMDNiv 	=	Max (0,Min((OLivq - MRivq ), NETDEQivq)) * OOMAGRivq

PEOOMDNiq	=	SUM (PEOOMDNiu)q + SUM (PEOOMDNiv)q

PEOOMDNiz	=	SUM (PEOOMDNiu)z + SUM (PEOOMDNiv)z

The equation below will be used to determine the Total OOM Down or Zonal OOM Down Payments to be allocated to each QSE in Section 6.9.7.2, OOM Energy Charge.

PEOOMDNi = SUM (PEOOMDNiq)q

NETDEQivq	=	Max [0, ((NETOOMDEQivq + NETLBEDQivq) –
(NETOOMUEQivq + NETLBEUQivq))]

NETOOMUEQivq 	=	Max(0, (SUM(IOOMUPqui)u – SUM(IOOMDNqui)u))

NETLBEUQivq 	=	Max(0, (SUM(LBEUQqui)u – SUM(LBEDQqui)u))

NETOOMDEQivq	=	Max(0, (SUM(IOOMDNqui)u – SUM(IOOMUPqui)u))

NETLBEDEQivq 	=	Max(0, (SUM(LBEDQqui)u – SUM(LBEUQqui)u))

OOMAGRivq	=	[SUM(IOOMUPqui)u + SUM(IOOMDNqui)u] / 
[SUM(LBEUQqui)u + SUM(LBEDQqui)u + 
SUM(IOOMUPqui)u + SUM(IOOMDNqui)u]

Where:

c	Resource category

i	interval

u	individual generation unit (including units within an Aggregated Unit)

v	Aggregated Unit

z	zone

q	QSE

PEOOMDNiuqz	Out of Merit Energy Down Payment ($) for that interval per unit for the QSE

PEOOMDNivqz	Out of Merit Energy Down Payment ($) for that interval per Aggregated Unit per QSE

PEOOMDNiq	Total Out of Merit Energy Down Payment in the interval for the QSE

PEOOMDNiz	Out of Merit Energy Down Payment ($) per interval per zone

PEOOMDNiv	Out of Merit Energy Down Payment ($) per interval per zone to Aggregated Units

EOOMDNiu 	OOM Energy quantity instructed down for that unit per interval

EOOMDNiv 	OOM Energy quantity instructed down for that Aggregated  Unit per interval

MCPEiz	Market Clearing Price for Energy per interval for that zone

IOOMUPiuq	OOM Energy Up Instructions for that interval for that unit converted to MWh for that interval by dividing by the interval count per hour (4 per hour for 15 minute Settlement Interval)

IOOMDNiuq	OOM Energy Down Instructions for that interval for that unit converted to MWh for that interval by dividing by the interval count per hour (4 per hour for 15 minute Settlement Interval)

MRiu	Meter reading per unit per interval

MRiv	Meter reading per Aggregated Unit per interval

OLiuq	Resource Plan submitted by the QSE for the specific unit given the OOM instruction for that interval.

[PRR426: Replace the definition above with the following upon system implementation:] OLiuq Resource Plan submitted by the QSE for the specific unit given the OOM instruction for that interval. If an Uncontrollable Renewable Resource has elected to use its Renewable Production Potential in lieu of its Resource Plan for OOME Down payments, this variable is equal to such Potential.

OLivq	Resource Plan submitted by the QSE for the Aggregated Unit containing the individual unit(s) given the OOM instruction for that interval.

RCGFCc	Resource Category Generic Fuel Cost for a specific category as defined in Section 6.8.2

PEOOMDNi	Total OOM Down Energy Payments

LBEUQqui	Local Balancing Energy Up Instructions for that interval per specific unit

LBEDQqui	Local Balancing Energy Down Instructions for that interval per specific unit

NETOOMUEQivq The net of all unit-specific OOM instructions (Up minus Down) that result in a positive value.

NETLBEUQivq	The net of all unit-specific Local Balancing Energy Instructions (Up minus Down) that result in a positive value.

NETOOMDEQivq The net of all unit-specific OOM instructions (Down minus Up) that result in a positive value.

NETLBEDQivq The net of all unit-specific Local Balancing Energy Instructions (Down minus Up) that result in a positive value.

NETDEQiv	The overall net direction per the instructions given to the Aggregated Unit results in a down direction

OOMAGRiv 	The percentage of the aggregated instructions to the Aggregated Unit that represents the OOM Energy market.

(6)	If a wind Resource is called upon to provide OOME Down Service and the normal payment for OOME Service is insufficient to cover actual verifiable costs of providing the service, then that Resource may file a claim with ERCOT to be paid the lower of:

(a)	All verifiable costs that are directly attributable to the OOME service; or

(b)	MaxCap * CCF * Curtail% * Hrs *CRP

Where:

MaxCap:	Registered Maximum Capacity of the Resource (MW)

CCF:	Capacity Conversion Factor as defined at 30%

Curtail%:	Set at 15% for the period July 1, 2002 through June 30, 2003; 10% for the period July 1, 2003 through June 30, 2004; and 5% from July 1, 2004 and thereafter.

Hrs:	Total number of hours in the month

CRP:	Price paid for curtailment, $27/MWH

The verifiable costs of providing the service shall be provided to ERCOT in writing from the QSE, certified by an authorized representative of the Resource and within a timeframe to allow resolution by the end of the dispute process for Settlement True-Up.  Verifiable costs under section (a) above shall be based on the actual verifiable MW production that the unit could have produced based on actual operating and maintenance conditions and actual wind speeds.  Verifiable costs must be established in order for a claim to be valid even if paid under method (b) above.

A wind Resource filing a claim under this Section 6.8.2.3(6) must provide actual production and actual wind speed data for the entire month of the claim.  ERCOT will review this data for all hours of the month.  In the event ERCOT determines that it paid the Resource for any OOME down service in any hour of the month that the actual wind speed data show could not have actually been provided, then ERCOT shall deduct any such excess payment from the payment otherwise payable under (a) or (b) above.  A wind Resource filing a claim under Section 6.8.2.3(6) shall also provide an affidavit indicating that the wind Resource, or its Affiliate(s), has tax liability sufficient to fully utilize any lost credits claimed to offset taxes for the year in which the credit would have been received.

This provision will expire at the earlier of:

(i)	December 31, 2006;

(ii)	When ERCOT implements direct assignment of Local Congestion costs in accordance with the PUCT’s Order on Rehearing in Docket 23220; or

(iii)	Within one (1) month after accumulated verifiable costs paid under this Section 6.8.2.3(5) reach ten million ($10,000,000) dollars.

(7)	Whenever a Load acting as a Resource is called for OOME Up, the QSE will receive an OOME payment of the instructed amount of OOME Up provided by the Load acting as a Resource multiplied by a price equal to item (a) minus item (b), as defined below:

(a)	The lower of the:

(i)	Sum of the bid premium submitted by the specific Load acting as a Resource and the MCPE for the Congestion Zone; or

(ii)	The OOME Up Price.

(b)	The MCPE for the Congestion Zone.

OOME Up Price is determined by multiplying the Fuel Index by the appropriate Heat Rate.  The Heat Rate will be set at 18 MMBtu / MWh.

The FIP shall be the midpoint price expressed in $ / MMBtu, published in Gas Daily, in the Daily Price Survey, under the heading “East-Houston-Katy, Houston Ship Channel” for the day of OOME deployment.  The FIP for Saturdays, Sundays, holidays, and other days for which there is no FIP published in Gas Daily, shall be the next published FIP after the day of OOME deployment.  In the event that the FIP is not published for more than two (2) days, the previous day published FIP will be used for Initial Settlement and the next day published FIP will be used for true up of the Final Statement.

The calculation for OOME Up for Load acting as a Resource is as follows:

PEOOMUPiq 	=	SUM (PEOOMUPiuq)uq

Where:

PEOOMUPiuq	=	-1 * EOOMUPiuq * [Max [Min ((FI * HR), (BPiuq + MCPEiz)), MCPEiz] - MCPEiz]

EOOMUPiuq	=	Max (0, Min (OLiuq - LAARTOT), IOOMUPiu))

The equation below will be used to determine the Total OOM Energy Payments to be allocated to each QSE in Section 6.9.7.2, OOM Energy Charge.

PEOOMUPi 	= SUM(PEOOMUPiu)

Where:

i		interval

q		QSE

u		unit

z		zone

FI		Fuel Index ($/Btu)

HR	The standard Heat Rate for OOM of a Load Acting as a Resource is 18 MMBtu

EOOMUPiuq	OOM Up quantity deployed for that unit per interval per QSE

IOOMUPiu	The difference between the Resource Plan and the OOM Energy Up Instructions for that interval for that unit converted to MWh for that interval by dividing by the interval count per hour (4 per hour for 15 minute Settlement Interval)

BPiuq	Actual Bid Premium Up bid price submitted by the specific Load acting as a Resource

LAARTOT	Actual ESI ID usage

MCPEiz	Market Clearing Price of Energy for that interval of the zone in which unit resides

OLiuq	Resource Plan output level submitted by the QSE for the specific Resource given the OOM instruction for that interval

PEOOMUPi	Summation of Out of Merit Energy Up Payment ($) per interval for all QSEs in the market

PEOOMUPiq	Out of Merit Energy Up Payment ($) for that interval per QSE

PEOOMUPiuq	Out of Merit Energy Up Payment ($) for that interval per unit per QSE

If a Load acting as a Resource is called to provide OOME Up service and the payment for OOME service is insufficient to cover all costs of providing the Service, then that Load acting as a Resource will be paid, in addition to the energy payment, all verifiable costs in excess of the OOME payment that are directly attributable to the OOME Service.  These costs may include the cost of lost raw material, product rendered unusable, idled labor, clean up cost associated with the deployment required to restart production. In addition incremental production cost such as labor, energy and material, as well as any incremental energy cost associated with running backup generation may also be included. Idled labor will only be allowed if the OOME instruction is longer than three (3) hours in duration. Such payment will not exceed one thousand dollars ($1000) per MWh for the duration of the deployment plus an additional restart period not to exceed three (3) hours.  Verification of these costs must be submitted to ERCOT to allow resolution by the end of the dispute process for Settlement True-Up as defined in Section 9.2.4, Final Statements, True-Up Statements.

Compensation for types of cost, whose documentation requirements are not outlined in this Section 6.8.2.3(7), must be reviewed and approved by the ERCOT Board of Directors during an Executive Session of their next regularly scheduled meeting.  Requests must be presented in person by a representative of the company submitting the request and must also include language suitable to be included in the Protocols to define the documentation requirements for future requests of a similar nature.  Subsequent to the approval of such costs, the requesting company shall submit a Protocol Revision Request, in accordance with Section 21, Process for Protocol Revision, incorporating the necessary documentation standards provided to the ERCOT Board. Once approved by the ERCOT Board, ERCOT will process payments for such cost on a Resettlement Statement as described in Section 9.2.5, Resettlement Statement.

6.8.2.4	Aggregating Units

(1)	Generation Entities in ERCOT may choose to request that ERCOT allow the Generation Resource to aggregate, for settlement purposes, two (2) or more individual units located at a single location if the operation of those units requires that an interdependent and coordinated relationship is maintained (for example, combined cycle operation).

(2)	ERCOT will review requests to have individual units aggregated into an Aggregated Unit for settlement purposes and will determine if the aggregation can be performed without negative impact to ERCOT’s operations.  Criteria ERCOT will use include, but are not limited to: (i) evaluation of Shift Factors of the units to be aggregated relative to Local Congestion in the same zone as the units to be aggregated; and (ii) whether the individual units connect to the same bus.  ERCOT shall have the sole discretion whether to approve the request to treat individual units as an Aggregated Unit for settlement purposes.

(a)	Requests for site-specific aggregation of units shall be prepared by the QSE representing the Generation Entity for the units using the appropriate form posted on the ERCOT MIS.  Once ERCOT approves aggregating the units into an Aggregated Unit for settlement purposes, the units may not be requested to be disaggregated for three hundred sixty-five (365) days from the date on which ERCOT approved the Aggregated Unit.

(b)	Treatment of individual generation units as an Aggregated Unit shall be for settlement purposes only and ERCOT’s Control Area Operators and its operations system and staff will continue to treat the individual units as individual units and will not recognize Aggregated Units.  By way of example only, ERCOT will continue to perform its reliability studies based on individual units and send Dispatch Instructions to individual units within an Aggregated Unit.

(3)	Once ERCOT approves the Aggregated Unit, ERCOT shall have fifteen (15) Business Days to establish the relationships in its settlement process to correctly settle the units as an Aggregated Unit.  The effect of the aggregation will be that all schedules, instructions, and actual metered output for the individual units of an Aggregated Unit will be added and ERCOT will use the sum in its settlement calculations for the QSE representing the Aggregated Unit.

(4)	Specifically:

EOOMUPivq 	= 	Sum(EOOMUPiuq)

IOOMUPiv 	= 	Sum(IOOMUPiu)

MRivq 	= 	Sum(MRiuq)

OLivq 	= 	Sum(OLiuq)

EOOMDNivq 	= 	Sum(EOOMDNiuq)

IOOMDNiv 	= 	Sum(IOOMDNiu)

Where:

i	interval

u	individual generation unit (including units within an Aggregated Unit).

v	Aggregated Unit

q	QSE

EOOMUPiuq	OOM Up quantity deployed for each unit in the Aggregated Unit per interval per QSE.

EOOMUPivq	OOM Up quantity deployed for the Aggregated Unit per interval per QSE.

IOOMUPiu	OOM Energy Up Instructions for that interval for that unit converted to MWh for that interval by dividing by the number of intervals per hour (4 per hour for 15 minute Settlement Intervals).

IOOMUPiv	OOM Energy Up Instructions for that interval for that Aggregated Unit converted to MWh for that interval by dividing by the number of intervals per hour (4 per hour for 15 minute Settlement Intervals).

MRiuq	Meter Reading for that unit for that interval per QSE.

MRivq	Meter Reading for that Aggregated Unit for that interval per QSE

OLiuq	Resource Plan output level submitted by the QSE for the specific unit given the OOM instruction for that interval.

OLivq	Resource Plan output level submitted by the QSE for the Aggregated Unit containing the individual unit(s) given the OOM instruction for that interval.

EOOMDNiuq	OOM Down quantity deployed for each unit in the Aggregated Unit per interval per QSE

EOOMDNivq	OOM Down quantity deployed for the Aggregated Unit per interval per QSE

IOOMDNiu	OOM Energy Down Instructions for that interval for the unit converted to MWh for that interval by dividing by the number of intervals per hour (4 per hour for 15 minute Settlement Intervals)

IOOMDNiv	OOM Energy Down Instructions for that interval for that Aggregated Unit converted to MWh for that interval by dividing by the number of intervals per hour (4 per hour for 15 minute Settlement Intervals)

6.8.2.5	Settlement of Zonal OOME Deployments

(1)	QSEs responding to Zonal OOME Up Dispatch Instructions will be paid OOME Up payments as set forth in Section 6.8.2.3, Energy Payments, paragraph (2).  The Resource-specific OOME Up payment for such Resource(s) will be included on the Initial Statement for the applicable Operating Day.  If ERCOT cannot timely prepare and import the billing determinants required to settle Zonal OOME Up prior to the issuance of the Initial Statement, ERCOT will settle the Zonal OOME Up Dispatch Instructions on the Final Statement for the affected Operating Day.   ERCOT will calculate the OOME Up payment based on the Generation Resource(s) that generated above its planned output level as indicated in the QSE’s Resource Plan.  If the QSE does not provide the total instructed amount of Zonal OOME Up Service, the QSE will be compensated for only the amount of the Zonal OOME Dispatch Instruction actually provided.

(2)	QSEs responding to Zonal OOME Down Dispatch Instructions will be paid OOME Down payments as set forth in Section 6.8.2.3, Energy Payments, paragraph (4).  The Resource-specific OOME Down payment for such Resource(s) will be included on the Initial Statement for the applicable Operating Day.  If ERCOT cannot timely prepare and import the billing determinants to settle Zonal OOME Down prior the issuance of the Initial Statement, ERCOT will settle the Zonal OOME Down Dispatch Instructions on the Final Statement for the affected Operating Day.  ERCOT will calculate the OOME Down payment based on the Generation Resource(s) that generated below its planned output level as indicated in the QSE’s Resource Plan.  If the QSE does not provide the total instructed amount of Zonal OOME Down Service, the QSE will be compensated for only the amount of the Zonal Dispatch Instruction actually provided.

(3)	Zonal OOME Up Service and Zonal OOME Down Service provided based on a Zonal Dispatch Instruction will not be subject to uninstructed Resource charges as described in Section 6.8.1.15.3, Uninstructed Charge Methodology and Equation.

[PRR454: Add Section 6.8.2.6 upon system implementation:] 6.8.2.6 Payment When a Resource Receives an OOME Down to Zero (0) MW Dispatch Instruction (1) Resources that are issued Dispatch Instructions to provide OOME Down Service to zero (0) MW, and which actually shut down to follow such Dispatch Instructions, will be paid both the OOME Cost defined in Section 6.8.2.3, Energy Payments, for the instructed interval(s) and Resource Category Generic Capacity Startup Cost for each instructed shut down. (2) Compensation for additional types of cost, not outlined above, must be reviewed and approved by the ERCOT Board of Directors during an Executive Session of its next regularly scheduled meeting. Requests must be presented in person by a representative of the company submitting the request and must also include language suitable to be included in the Protocols to define the documentation requirements for future requests of a similar nature. Subsequent to the approval of such costs, the requesting company shall submit a Protocol Revision Request, in accordance with Section 21, Process for Protocol Revision, incorporating the necessary documentation standards provided to the ERCOT Board. (3) The calculation of startup payment for the Resource that receives an OOME Down Dispatch Instruction to provide service to zero (0) MW is: PSu = RCGSCc Where: PSu Startup payment for the Resource which receives an OOME Down Dispatch Instruction to zero (0) MW c Resource Category u Single Resource RCGSCc Resource Category Generic Startup Cost for a specific category of generation unit

6.8.3	Capacity and Energy Payments for RMR and Synchronous Service

RMR Units and MRA resources selected through the planning process, pursuant to Section 6.5.9.2, Exit Strategy from an RMR Agreement, providing services will be paid according to their Agreement.

6.8.3.1	Capacity Payments for RMR Service

(1)	The capacity payment for RMR Service is referred to in these Protocols as the “Standby Price.”  The hourly Standby Price to be used in settlement will be calculated as follows:

SBRMRhq	=	Σ(SBRMRuhq)u

SBRMRuhq	=	-1 * AvailRedu * StbyPriceu * BillCapuh

AvailGenCapuhi	=	MIN (AvailPlanCapuh, MiscondCapuh, MaxGenCapuh)

AvailRedu	=	IF (HrRollEAFuh >= TA, 1, IF(HrRollEAFuh > .35, (1-((TA - HrRollEAFuh)*2)), 0)

BillCapuh 	=	IF (TestCapu < RMRCapu, RMRCapu *(1 – TestCapRedu), RMRCapu)

HrRollEAFuh	=	IF (Elapsed Hours < 4379, 1, ((AvailGenCapuh + ∑AvailGenCapuh /(MaxGenCapuh + (∑MaxGenCapuh4379))

MaxGenCapu	=	MIN (RMRCapu, TestCapu)

MiscondCapuh		=	IF (AMDuh >= (.98 * AvailPlanCapuh),
AvailPlanCapuh, AMDuh)

TestCapReduh	=	((RMRCapu – TestCapuh)/RMRCapu)*2

Where:

i		interval

h		hour

u		unit

AMDuh	=	Actual Metered Delivery per unit per hour in MW

AvailPlanCap	=	Available Capacity per the Availability Plan

Elapsed Hours	=	Elapsed hour since 0000 of the date of contract inception

MiscondCapuh	=	IF (MiscondExcused = No, (IF (AMDuh > (.98 * AvailPlanCapuh), 0, 10000), 0)

MiscondExcused	=	Yes or No

RMRCapu	=	Maximum unit capacity as stated in the RMR Contract.

StbyPriceu	=	Hourly Standby Price for the RMR as stated in the RMR Agreement

TA		= 	Target Availability defined in Section 6.8.3.1(5)

TestCapuh	=	Test Capacity is the capacity resulting from test conducted by ERCOT.

Note:  If less than 4380 hours have elapsed since the start date, 
HrRollEAFui = 1.0

(2)	The formula below will be used to determine the total RMR Payments to be allocated to each QSE in Section 6.9.4, Settlement Obligation for Black Start Service, RMR Standby Service, and RMR Synchronous Condenser Service.

SBRMRi	=	SUM(SBRMRuhq)q / n

Where:

i	interval

h	Hour

n	number of intervals in the hour

q	QSE

u	unit

SBRMRi	Summation of RMR Standby Prices in that interval for all QSEs in the market

SBRMRuhq	RMR Standby Price per unit (for that QSE) for that hour

(3)	The hourly Standby Price will be based on the estimated Eligible Costs of the RMR Unit as contained in the RMR Agreement.  The monthly estimate will be adjusted to actual Eligible Costs prior to the True-Up Settlement Statement.  An Incentive Factor will be applied to the actual Eligible Costs, excluding fuel costs, incurred by the RMR Unit in the provision of RMR Service.  Actual cost data must be submitted on time by the Generation Entity for the RMR Unit and then verified by ERCOT so the actual cost data can be reflected in the True-Up Settlement Statement.  To be considered timely, actual cost data for month ‘x’ must be submitted thirty (30) days prior to the publishing date of the True-Up Settlement Statement for the first day in month ‘x.’

SBRMRmu =	[monthly estimate +/- adjustment for Eligible Costs + incentive factor]/h

Where:

h	hours in the month

m	month

u	unit

(4)	“Eligible Costs” for annual RMR Agreements, RMR Agreements for the minimum agreement period and RMR Agreements under Section 6.5.9, Reliability Must-Run Service, item (5) for periods exceeding twelve (12) months are defined to be costs that would be incurred by the RMR Unit owner to provide the RMR Service, excluding fuel costs, above the costs the RMR Unit would have incurred anyway had it been mothballed or shut down.  Examples of appropriate Eligible Costs include, but are not limited to, the following to the extent they each meet the standard for eligibility:

(i)	Labor, materials, supplies and services necessary to operate the RMR Unit;

(ii)	Costs associated with emissions credits or emissions reduction equipment;

(iii)	Costs associated with maintenance due to either required equipment maintenance or replacement to alleviate unsafe operating conditions, regulatory requirements, or to ensure the ability to operate the RMR Unit consistent with Good Utility Practice;

(iv)	Reservation and transportation costs associated with firm fuel supplies not recovered under Section 6.8.3.3, RMR Energy Payments Based on Contract Amounts;

(v)	Property taxes and other taxes attributable to continuing to operate the RMR Unit; and

(vi)	Capital Expenditures and associated debt and interest cost, if applicable, required to keep the RMR Resource available for RMR as negotiated with ERCOT.  The salvage value of any Capital Expenditure will be rebated to ERCOT at the end of the contract term.

Examples of costs not included as Eligible Costs are:

(i)	Depreciation expense for any Capital Expenditures incurred prior to the execution of an RMR , depreciation expense for any Capital Expenditures not approved in advance by ERCOT,  debt and interest costs incurred prior to the execution of an RMR Agreement;

(ii)	Property taxes and other taxes not attributable to continuing to operate the RMR Unit;

(iii)	Labor costs associated with other, non-RMR Generation Resources at the same Facility; and

(iv)	Any other costs the Generation Entity would have incurred even if the RMR Unit had been mothballed or shutdown.

(5)	The owner of the RMR Unit shall provide good faith detailed estimates of its non-fuel Eligible Costs to ERCOT as part of the RMR Agreement negotiation process.  ERCOT shall review and approve the budget and utilize these figures as the basis for Initial Settlement for RMR Service.  Actual Eligible Costs incurred by the RMR Unit will be used for on subsequent Final, Resettlement, or True-Up Settlements as agreed upon in Section 6.8.3.1(6).

The non-fuel Eligible Cost budgeting process shall be as follows:

RMR Unit owner shall supply ERCOT a preliminary non-fuel Eligible Cost budget for the twelve (12) month period starting with the anticipated effective date of the RMR Agreement.  The budget will include Eligible Costs categorized in terms of (i) Base Cost of Operations; (ii) Outage Maintenance Cost; (iii) Non Outage Maintenance Cost; and (iv) Other Budget Items, each of which are further defined as follows:

(i)	“Base Cost of Operations” includes Eligible Costs that are independent of the levels of operation, Outages and non-Outage maintenance;

(ii)	“Outage Maintenance Cost” includes Eligible Costs attributable to scheduled Outages and/or inspections occurring during the term of the RMR Agreement.  Maintenance alternatives available during any scheduled Outage will be presented to ERCOT for determination of the alternative to be performed and paid for under the RMR Agreement.  The RMR Unit owner will present ERCOT with a budget for each option, benefits of each alternative, unit availability impact associated with not performing each alternative, and a recommendation to facilitate ERCOT’s selection process;

(iii)	“Non-Outage Maintenance Cost” includes non-recurring Eligible Costs that are independent of a particular scheduled Outage.  Non-Outage maintenance alternatives available during any scheduled Outage will be presented to ERCOT for determination of the alternative to be performed and paid for under the RMR Agreement.  The RMR Unit owner will present ERCOT with a budget for each option, benefits of each alternative, unit availability impact associated with not performing each alternative, and a recommendation to facilitate ERCOT’s selection process; and

(iv)	“Other Budget Items” include other Eligible Costs not clearly identifiable to the previous three categories.

Thirty (30) days after receipt of the preliminary non-fuel Eligible Costs budget, ERCOT shall notify the RMR Unit owner of its selections under the alternatives provided in the preliminary budget.  The RMR Unit owner and ERCOT will set the Target Availability consistent with the options presented to and selected by during the budgeting process.

(6)	The RMR Unit owner will provide ERCOT with actual Eligible Costs on a monthly basis in a level of detail sufficient for ERCOT to verify that all Eligible Costs are appropriate.  ERCOT will perform a true-up of the estimated Eligible Costs using the submitted and verified actual Eligible Costs for the RMR Unit on a schedule determined during the RMR contract negotiations such that, for the duration of the RMR Agreement, the QSE for the RMR Unit is paid only for the actual Eligible Costs incurred.  Documentation to be provided by an RMR Unit owner to allow ERCOT to verify submitted costs to ERCOT for payment will be based on mutual agreement between the RMR Unit owner and ERCOT or through specific documentation standards outlined in the Protocols.  Absent specific documentation requirements mutually agreed to by the parties or outlined in the Protocols, the RMR Unit owner will provide an affidavit as verification attesting that the Eligible Costs figures being submitted are attributable to operating the RMR Unit.

(7)	The Incentive Factor for all RMR Agreements is equal to ten percent (10.0%) of the actual Eligible Costs incurred by the RMR Unit for the duration of the RMR Agreement.  The Incentive Factor will be paid at the same time as the actual Eligible Costs.  The Incentive Factor for RMR Agreements shall not be applied to any debt payment or interest costs.

(8)	The Incentive Factor payment may be reduced if the RMR Unit fails to perform to the contracted capacity during a Capacity Test as described in the RMR Agreement.  The reduction will be linear, with a two percent (2%) reduction in the Incentive Factor payment for every one percent (1%) of reduced capacity.

(9)	During the term of an RMR Agreement, in the event that major equipment modifications are required in order for the RMR Unit to provide RMR Service (such as installation of SCR equipment to meet NOx limitation requirements), ERCOT and the RMR Unit owner may negotiate an alternate Standby Price and/or term longer than one (1) year.

(10)	The Incentive Factor payment may be reduced if the RMR Unit fails to perform at the Target Availability, established during the budgeting process outlined in section 6.8.3.1 (5) above, for a rolling six (6) month average.  The reduction will be linear; with a two percent (2%) reduction in Incentive Factor payment for every one percent (1%) that availability is less than the Target Availability of the contracted capacity.

6.8.3.2	Capacity Payments for Synchronous Condenser Service

Any capacity provided by Synchronous Condensers will not be compensated.

[PIP128: The system is not configured to compensate for Synchronous Condenser Service.] Synchronous Condenser Agreements are set annually. An economic model will be used, identical to RMR economic model defined above in Section 6.8.3.1, Capacity Payments for RMR Service, to determine the levelized (i.e., same cost each year) annual carrying costs of a then current simple-cycle gas turbine generator set (class and size to be defined to approximately equal the megawatts or megavolt-amps being contracted). (1) The annual total costs derived from the economic model described above will be converted to an hourly cost by dividing it by eight thousand seven hundred sixty (8,760) hours. (2) For Synchronous Condenser Units, the hourly cost derived in (1) is multiplied by twenty percent (20%) and divided by the nameplate megavolt-amps (MVA) size for the proxy unit. This yields the hourly standby price for Synchronous Condensers. (3) The standby price may be reduced if the Synchronous Condenser Unit fails to perform at eighty-five percent (85%) availability for a rolling six (6) month average. The reduction will be linear, with a two percent (2%) reduction in standby fee for every one percent (1%) that availability is less than eighty-five percent (85%) of the contracted capacity. (4) The settlement calculation to determine the Synchronous Condenser standby fee is as follows: SSBqh = SUM(SSBuhq)u Where: SSBuh = -1 * HrPrice * SCUCapuhi *AvailReduh SCUCapuh Synchronous Condenser Unit Capacity is the capacity that is used in determining the Standby Fee based on contract MVA AvailReduh = IF (HrRollEAFuh >=.85, 1, IF (HrRollEAFuh >.35, (1 – ((.85 – HrRollEAFuh) * 2)), 0)) Availability Capacity Reduction is the reduction in Billing Capacity caused by the unit being less than eighty-five percent (85%) available on a rolling six month basis. HrRollEAFui = ((∑h=1-4380 AvailSyncuh) / 4380) Hourly Rolling Equivalent Availability Factor over a rolling six month period. AvailSyncui = Y; Available of service. Where: Y = 0 for unavailable service Y = 1 for available service MiscondChrg = IF (Excused = Yes, 0, 10000) (5) The formula below will be used to determine the total Synchronous Condenser Payments to be allocated to each QSE in Section 6.9.4, Settlement Obligation for Black Start Service, RMR Standby Service, and RMR Synchronous Condenser Service. SSBi = SUM(SSBhq)q / n Where: h hour n number of intervals in an hour SSBuhq Synchronous Condenser Standby Payment per Unit per hour for that QSE SSBqh Synchronous Condenser Standby Payment per hour to the QSE. SSBi Summation of Synchronous Condenser Standby Payments per interval for all QSEs in the market MiscondChrg When not excused, currently set at ten thousand ($10,000) dollars per day. Note: If less than 4380 hours have elapsed since the start date, HrRollEAF = 1.0

6.8.3.3	RMR Energy Payments Based on Contract Amounts

(1)	Fuel payments, on the Initial Settlement Statement, for energy delivered under the RMR Agreement will be based on the product of such energy delivered (in MWH) times an estimated RMR Unit heat rate, in MMBtu/MWh, times an estimated fuel price, in $/MMBtu as included in the contract amount negotiated by the Generation Entity.  The fuel payment will be subsequently trued-up to reflect actual fuel costs as set forth in Section 6.8.3.3(4).

(2)	The RMR Unit owner shall provide good faith estimates of the RMR Unit heat rate to ERCOT in its application for an RMR Agreement.  Based on production figures provided to the RMR Unit owner by ERCOT, the RMR Unit owner shall also provide ERCOT fuel Supply options available for the RMR Resource.  For each option, RMR Unit owner will detail the associated impacts on the fuel and non-fuel budgets and on the availability of the unit.  No less than thirty (30) days after the receipt of the fuel Supply options, ERCOT shall notify the RMR Unit owner of its fuel Supply option selection.  Fuel payments on the Initial Settlement Statement for RMR Services provided will be based on the estimated heat rates, actual RMR energy deployments, and estimates of fuel costs established using the fuel Supply options selected by ERCOT.  These payments will be trued up to reflect actual verifiable fuel costs incurred by the RMR Unit on subsequent Final, Resettlement or True-Up Statements as outlined in Section 6.8.3.3(4).

(3)	The Generation Entity in good faith may revise the estimated fuel prices for its RMR Unit at any time to more accurately reflect the expected fuel expense for a particular day, subject to ERCOT’s approval of the revised fuel price, which ERCOT shall not unreasonably withhold.  This adjusted fuel price will be the basis for payment for energy delivered in the operating month, subject to true-up by ERCOT based on actual fuel costs incurred by the RMR Unit in providing RMR Service.

(4)	The RMR Unit owner shall provide ERCOT with actual fuel costs on a monthly basis for the RMR Unit in a level of detail sufficient for ERCOT to verify that all fuel costs are actual and appropriate.  ERCOT will perform a true-up of the estimated fuel costs using the submitted and verified actual fuel costs for the RMR Unit on a schedule determined during the RMR Agreement negotiations such that, for the duration of the RMR Agreement, the RMR Unit is paid only for its actual fuel costs incurred.  Documentation to be provided by an RMR Unit owner to allow ERCOT to verify submitted fuel costs to ERCOT for payment will be based on mutual Agreement between the RMR Unit owner and ERCOT or through specific documentation standards outlined in the Protocols.  Absent specific documentation requirements mutually agreed to by the parties or outlined in the Protocols, the RMR Unit owner will provide an affidavit as verification attesting that the fuel cost figures being submitted represent fuel cost attributable to operating the RMR Unit.

(5)	Fuel costs incurred by the RMR Unit to provide Balancing Energy Service will be excluded from the monthly fuel cost payment.  The amount to be excluded will be calculated by multiplying the total actual fuel cost for the month by the monthly energy produced for Balancing Energy Service and then divided by the total energy produced by the RMR Unit for the month.

(6)	The formula below will be used to determine the total RMR Payments to be allocated to each QSE in Section 6.9.4, Settlement Obligation for Black Start Service, RMR Standby Service, and RMR Synchronous Condenser Service.

ERMRiq	=	SUM(ERMRui)q

Where:

i	interval

u	unit

q	QSE

ERMRiq	Summation of payments for RMR Energy per interval for all QSEs in the market.

ERMRui  	Payment to provider for RMR Energy per unit per interval

MRiu 	Metered value for the Resource per interval for that RMR Unit using actual and/or estimated values.

6.8.3.4	Synchronous Condenser Hourly Operations Payment

There will be no compensation for the operations of Synchronous Condensers

[PIP128: System Design does not support compensation for any Synchronous Condenser Service.] (1) For Synchronous Condenser Units, hourly operations payments shall be based upon the non-fuel variable O&M cost incurred when the unit operates and which is not recovered in the Standby Price as defined in item (1) of Section 6.8.3.1, Capacity Payments for RMR Service, above. The Hourly Operation Price can include: (a) Verifiable labor, materials, fees, taxes, etc. that are only incurred when the unit operates; plus (b) Payment for metered electricity consumed during the Settlement Interval. Compensation for electricity consumed shall be at a price per MWH equal to the Market Clearing Price for the interval and zone. (2) Payment for Synchronous Condenser Operations shall be calculated in the following manner: RunFeeqi = SUM(RunFeeuiq)u Where: RunFeeui = -1 * Runningui * RunPru (3) The formula below will be used to determine the total Synchronous Condenser Payments to be allocated to each QSE in Section 6.9.4, Settlement Obligation for Black Start Service, RMR Standby Service, and RMR Synchronous Condenser Service. RunFeei = SUM(RunFeeqi)q Where: RunFeeuiq Fee paid to Synchronous Condensers for each hour they run per interval per unit (for that QSE). RunPru Contractual Price Running $/Hour Runningui Running = 1 if unit is synchronized with the grid during any part of the hour. RunFeeqi Fee paid to QSEs representing Synchronous Condensers per interval RunFeei Summation of fees paid to QSEs representing Synchronous Condensers per interval for all QSEs in the Market

6.8.3.5	[Subsection currently not used]

6.8.3.6	Synchronous Condenser Start-Up Payment

There will be no compensation made for the start-up of a Synchronous Condenser Unit.

[PIP128: System design does not support compensation for SC Units] SCURMRiu = -1 * StartPru * Niu SCURMRiq = SUM(SCURMRiu)q Where: u unit i Interval q QSE Niu One (1) if a start is required by ERCOT in this interval. Zero otherwise. SCURMRiu RMR SC Startup Payment ($) for unit SCURMRiq RMR Startup Payment ($) for all units belonging to a QSE StartPru Contractual Amount for one start

6.8.3.7	RMR Excess Energy Rebates Outside of Contract Amounts

(1)	If the RMR Unit generates energy in excess of the amount it is obligated to produce (i.e., the difference between the energy produced less the scheduled amount for any Settlement Interval is positive), the rebate of the excess amount produced will be based on the Owner’s election of the Excess Energy Rebate Option in the RMR Agreement.  The Excess Energy Rebate Options are based on the appropriate rebate to the Gross Revenue or Net Positive Margin, as follows:

Option (A):  The net payment for energy above scheduled energy is based on the Market Clearing Price of Energy (MCPE) for the appropriate Settlement Interval and Congestion Zone (as described in Section 6.8.1.13), less an energy rebate, as described below.  Currently the approved Gross Revenue-based energy rebate percentage is equal to ten percent (10%) of the Gross Revenue.

Option (B):  The net payment for energy above scheduled energy is based on the MCPE (as described in Section 6.8.1.13), less an energy rebate of a percentage of the Net Positive Margin for energy.  The Net Positive Margin for energy is the product of the positive difference between the Market Clearing Price for Energy (MCPE) and the RMR Energy Price times the amount of MWh delivered above the scheduled amount.  Currently the approved Net Positive Margin-based energy rebate percentage is equal to ninety percent (90%) of the Net Positive Margin.

(2)	Option (A):  The rebate to ERCOT for RMR energy generated outside of the RMR Agreement terms under Option (A) above, shall be calculated in the following manner:

ERRMRiu	= [Max (0, (MRiu  - RSiu)) * MCPEiz * GRRP]

ERRMRiq	=	SUM (ERRMRiu)q

Where:

i	interval

u	unit

z	zone

ERRMRiu	RMR Energy Rebate Amount for that interval for that unit

ERRMRiq	RMR Energy Rebate Amount for that interval for that QSE

MRiu:	Metered value for the Resource per interval for that unit using actual and/or estimated values.

RSiu	Resource Scheduled quantity for that RMR Unit per interval

MCPEiz	Market Clearing Price for Energy per interval in that zone

GRRP	Approved Gross Revenue-based Rebate Percentage (currently 10%)

(3)	Option (B):  The rebate to ERCOT for RMR energy generated outside of the Agreement terms under Option (B) above, shall be calculated in the following manner:

ERRMRiu	= [Max (0, (MRiu  - RSiu)) * [Max (0, (MCPEiz - RMREriu))] * MRP]

ERRMRiq	=	SUM (ERRMRiu)q

Where:

i	interval

u	unit

z	zone

ERRMRiu	RMR Energy Rebate Amount for that interval for that unit

ERRMRiq	RMR Energy Rebate Amount for that interval for that QSE

MRiu:	Metered value for the Resource per interval for that unit using actual and/or estimated values.

RSiu	Resource Scheduled quantity for that RMR Unit per interval

MCPEiz	Market Clearing Price for Energy per interval in that zone

RMREriu	RMR Energy Price per interval per unit

MRP	Approved Net Positive Margin-based Rebate Percentage (currently 90%)

(4)	In accordance with Section 4.5.11.4, Receipt of QSEs Balancing Energy Bid Curves for RMR Unit, QSEs submitting Balancing Energy Service, bids using RMR Units, must keep the bids from RMR Units independent of other Balancing Energy Service bids.

6.8.3.8	RMR Non-performance for Unexcused Misconduct

(1)	If a misconduct event is not excused, then to reflect this lower-than-expected quality of firmness, ERCOT charges the QSE that represents the RMR Unit an Unexcused Misconduct Amount as defined in the RMR Agreement for each RMR Unit.

UMRMRiu   = 	 Fee * UMF

UMRMRiq	=	SUM(UMRMRiu)q

Where:

i	interval to be calculated

u	unit

UMRMRui	RMR Unexcused Misconduct event per unit for that interval

UMRMRiq	RMR Unexcused Misconduct Fee for all units represented by that QSE in that interval

UMF 	One if an Unexcused Misconduct Event occurred during that Operating Day otherwise zero.

Fee	Misconduct charge as specified in the RMR Agreement.

6.8.3.9	Synchronous Condenser Non-Performance for Unexcused Misconduct

(1)	If a misconduct event is not excused, then to reflect this lower-than-expected quality of firmness, ERCOT charges the Entity an Unexcused Misconduct Amount as defined in the SCU Agreement for each SCU Unit.

UMSCUiu  = 	 Fee * UMF

UMSCUiq	=	SUM(UMSCUiu)q

Where:

i	interval to be calculated

u	unit

UMSCUui	SCU Unexcused Misconduct event per unit for that interval

UMSCUiq	SCU Unexcused Misconduct Fee for all units represented by that QSE in that interval

UMF 	One if an Unexcused Misconduct Event occurred during that Operating Day otherwise zero.

Fee	Misconduct charge as specified in the SCU Agreement.

6.8.4	Capacity Payments for Voltage Support Provided to ERCOT

(1)	Reactive Support:  For Generation Resources required to provide VSS, Generation Entities will be required to maintain a voltage regulation schedule without compensation, limited to the quantity of Reactive Power the Generation Resources can produce at rated capability (MW), known as Unit Reactive Limit (URL).  ERCOT may instruct Generation Resources to exceed their URL, without compensation, if reliability of the ERCOT System is at risk; and

(2)	Power Reduction:  Unit-specific Dispatch Instructions given to reduce real power in order to allow Voltage Support will be settled as OOME Down, specified in Section 6.8.2.3(5), Energy Payments, of these Protocols.

[PRR409; upon system implementation, replace Section 6.8.4 with the following.] (1) Uncompensated Reactive Support – Generation Entities will be required to maintain a voltage regulation schedule without compensation limited to the quantity of Reactive Power the Generation Resource can produce at rated capability, (MW), and a power factor of 0.95 leading or lagging at rated MW output measured at the point of interconnection to the TSP. (2) Compensated Reactive Support – If ERCOT instructs the Generation Resource to exceed a power factor of 0.95 leading or lagging at rated MW output measured at the point of interconnection to the TSP, and the Generation Resource provides additional Reactive Power, then ERCOT will pay for the additional Reactive Power provided at a price that recognizes the avoided cost of reactive support Resources on the transmission network. For the following equations, URL shall be that level of Reactive Power that results in a power factor of 0.95 leading or lagging at rated MW output measures at the unit main transformer high voltage terminals regardless of the type or age of the Resource. For Reactive Power deployments above Generation Site URL: VARPAYAMTsqi = -1*(VP*MVARINSsqi) Where: MVARINSsqi = Max {0, (Min [VSOOMsqi, MVARsfi] – MVARS URLi)} And: MVARS URLi = Sum (MVAR URLi) Where: MVARINSsqi Amount of instructed MVARh produced by a Generation Resource that are above the sum of the Unit’s URLh during Settlement Interval i. MVARsfi Netted Metered Generation Resource Site Reactive Energy measured during the verbal deployment per interval. MVARS URLi Sum of all On-line Generation Resource URLh at the site per interval (MVARh). VSOOMsqi Reactive Power Instructed Level per site per SQE per interval (MVARh). MVARURLi Generation Resource Unit specific leading or lagging URLh at the site per interval. VP $/MVARh price for instructed MVAR beyond a Generation Resource’s site URL currently is $2.65/MVARh (based on $50.00/installed kVAR) with the exception of hydro Resources in the synchronous condenser mode. VARPAYAMTsqi The amount of payment in dollars for each Generation Resource site in Settlement Interval I that is Dispatched beyond its URL. VARPAYAMTqi The aggregated VARPAYAMTsqi in Settlement Interval i for each QSE. VARPAYAMTi The aggregated VARPAYAMTsqi uplifted to the market in Settlement Interval i. Note: URLu The quantity of Reactive Power a Generation Resource can produce at rated capability, (MW), and a power factor of 0.95 leading or lagging measured at the unit main transformer high voltage terminals. (3) Compensation for Power Reduction – Compensation for real power reduction to allow voltage support will be compensated as OOME Down, as specified in Section 6.8.2.3(5), Energy Payments, of these Protocols.

6.8.5	Capacity Payments for Resources Supplied to ERCOT for Black Start Service

(1)	ERCOT will pay an hourly standby fee, determined through a competitive annual bidding process, with an adjustment for reliability based on a six (6) month rolling availability equal to eighty-five percent (85%) in accordance with the Black Start Agreement in Section 22, ERCOT Protocols Agreements.

(2)	The calculation for Black Start is as follows:

PCBSui 	= 	-1 * (BillPctui * BSCPu)

PCBSqi 	= 	-1 * SUM (BillPctui * BSCPu)u

BillPctui 	= 	IF (HrRollEAFui >= .85,1,IF (HrRollEAFui  > .35, - (1- ((.85-HrRollEAFui) * 2)), 0))

HrRollEAFui 	= 	((∑h=1-4380 AvailBlkui) / 4380)

AvailBlkui 	= 	Y

Where:

Y = 0 for unavailable service

Y = 1 for available service

Where:

i	interval

u	single Resource

BSCPu	Black Start Contract Price of that single Resource

PCBSqi	Procured Capacity Payment for Black Start Service per interval for the QSE

BillPctui	Reduced Percentage of payment due to less than eighty-five percent (85%) availability.

HrRollEAFui	Hourly Rolling Equivalent Availability Factor over a rolling six-month period.

AvailBlkui	Available of service

(3)	The formula below is used to determine the total Black Start Payments to be allocated to each QSE in Section 6.9.4, Settlement Obligation for Black Start Service, RMR Standby Service, and RMR Synchronous Condenser Service.

PCBSi 	= 	SUM (PCBSiq)q

PCBSqi = SUM (PCBSiu)q

Where:

i	interval

u	single Resource

BSCPu	Black Start Contract Price of that single Resource

PCBSqi	Procured Capacity Payment for Black Start Service per interval for the QSE

PCBSui	Procured Capacity Payment for Black Start Service per interval per single Resource.

PCBSi	Summation of fees paid to QSEs providing Black Start Service per interval for all QSEs in the market

Note:  If less than 4380 hours have elapsed since the start date, 
HrRollEAF = 1.0

6.9	Settlement for ERCOT-Provided Ancillary Services

6.9.1	Settlement for ERCOT Ancillary Service Capacity Procured in the Day Ahead and Adjustment Periods

(1)	ERCOT shall allocate to each QSE representing Load its portion of the total ERCOT requirement of each of the Ancillary Services of Regulation Up, Regulation Down, Responsive Reserve Service, and Non-Spinning Reserve Service.  For settlement purposes, the QSE’s total capacity allocation shall be based on the QSE’s most recently calculated hourly Load Ratio Share for the applicable Operating Day.

(2)	The QSE’s settlement capacity shall be the QSE’s total capacity allocation minus any self-arranged Resources scheduled.

(3)	Each QSE’s settlement charge (or imbalance), in dollars, for each Ancillary Service, by hour, shall be equal to the MCPC for the Ancillary Service (in dollars per megawatt), and multiplied by the QSE’s settlement capacity (in megawatts).

(4)	There is no difference in the manner in which costs for procurement in the Day Ahead and Adjustment Period are allocated for the following services:

(a)	Regulation Up;

(b)	Regulation Down;

(c)	Responsive Reserve; and

(d)	Non-Spinning Reserve.

6.9.1.1	Regulation Up Service Charge

(1)	All costs of ERCOT procurement of Regulation Up shall be calculated as follows:

LARUqi 	=	RUPi * NTORUqi

RUPi 	=	((PCRUi + PCIESRUi  ) * -1 / (COBRUti – SARUti))

NTORUqi 	= 	(COBRUqi – SARUqi)

Where:

i	interval being calculated.

LARUqi	Regulation Up Service Capacity Load Allocation Charge ($) per interval for that QSE.

PCRUi	Procured Regulation Up Capacity Costs ($) for the total Market.

PCIESRUi	Emergency Service Regulation Up Capacity Costs ($) for the total Market for the interval.

COBRUqi	Obligated Regulation Up Capacity (MW) per interval of that QSE based on the QSE’s most recently calculated hourly Load Ratio Share.

COBRUti	Total Regulation Up Obligations Capacity (MW) in that interval.

SARUti	Total Self Arranged Regulation Reserve Up Capacity (MW) in that interval.

SARUi	Self Arranged Regulation Up Capacity (MW) Service per interval for that.

QSERUpi	Regulation Up Price per interval.

RUPi	Regulation Up Price per interval.

NTORUqi	Regulation Up Net Obligation (MW) per QSE per interval.

6.9.1.2	Regulation Down Service Charge

(1)	All costs of ERCOT procurement of Regulation Down shall be calculated as follows:

LARDqi 	=	RDPi * NTORDqi

RDPi 	=	((PCRDi + PCIESRDi  ) * –1 / (COBRDti – SARDti))

NTORDqi 	= 	(COBRDqi – SARDqi)

Where:

i	interval being calculated

LARDqi	Regulation Down Service Charge per interval Regulation Down Reserve Capacity Load Allocation Charge ($) per interval for that QSE

PCRDi	Procured Regulation Down Capacity Costs ($) for the total Market for the interval

PCESRDi	Emergency Service Regulation Down Capacity Costs ($) for the total Market for the interval

COBRDqi	Obligated Regulation Down Capacity (MW) Service per interval of that QSE based on the QSE’s most recently calculated hourly Load Ratio Share

SARDqi	Self Arranged Regulation Down Capacity (MW) Service per interval of that QSE

RDPi	Regulation Down Price per interval

NTORdqi	Regulation Down Net Obligation (MW) per QSE per interval

COBRDti	Total Regulation Down Obligations in that interval.

SARDti	Total Self Arranged Regulation Down in that interval

6.9.1.3	Responsive Reserve Service Charge

(1)	All costs of ERCOT procurement of Responsive Reserve shall be calculated as follows:

LARRqi 	=	RRPi  * NTORRqi

RRPi 	=	(PCRRi + PCIOOMRRi)  * -1 / (COBRRti – SARRti)

NTORRqi	=	(COBRRqi - SARRqi)

Where:

i:	interval being calculated

LARRqi	Responsive Reserve Capacity Load Allocation Service Charge ($) per interval for that QSE

PCRRi	Procured Responsive Reserve Capacity Costs ($) for the total Market for the interval

PCOOMRRi	Out of Merit Responsive Reserve Capacity Costs ($) for the total Market for the interval

COBRRqi	Obligated Responsive Reserve Capacity (MW) Service per interval of that QSE based on the QSE’s most recently calculated hourly Load Ratio Share

SARRqi	Self Arranged Responsive Reserve Capacity (MW) Service per interval of that QSE

RRPi	Responsive Reserve Price per interval

NTORRqi	Responsive Reserve Net Obligation (MW) per QSE per interval

COBRrti	Total Responsive Reserve Obligations Capacity (MW) in that interval.

SARRti	Total Self Arranged Responsive Reserve Capacity (MW) in that interval

6.9.1.4	Non-Spinning Reserve Service Charge

(1)	All costs of ERCOT procurement of Non-Spinning Reserve shall be calculated as follows:

LANSqi 	=	NSPi  * NTONSqi

NSPi  	=	((PCNSi + PCIOOMNSi) * -1  / (COBNSti – SANSti))

NTONSqi	=	(COBNSqi – SANSqi)

Where:

i	interval being calculated

LANSqi	Non-Spinning Reserve Capacity Load Allocation Charges ($) per interval for that QSE

PCNSi	Procured Non-Spinning Reserve Capacity Costs ($) for the total Market for the interval

PCESNSi	Emergency Service Non-Spinning Reserve Capacity Costs ($) for the total Market for the interval

COBNSti	Total Non-Spinning Reserve Obligations Capacity (MW) in that interval.

SANSti	Total Self Arranged Non-Spinning Reserve in that interval

COBNSqi	Obligated Non-Spinning Reserve Capacity (MW) per interval of that QSE based on the QSE’s most recently calculated hourly Load Ratio Share.

SANSqi	Self Arranged Non-Spinning Reserve Capacity (MW) per interval of that QSE

NSpi	Non-Spinning Reserve price per interval

NTONSqi	Non-Spinning Reserve Net Obligation (MW) per QSE per interval

6.9.1.5	Settlement of ERCOT Ancillary Services Capacity Procured for Defaulted AS Obligations

(1)	ERCOT shall allocate to each QSE, who has defaulted on their Ancillary Service Supply Obligation, their proportionate share of the cost of resolving the default.  ERCOT shall assign default charges in the appropriate Adjustment Period.  When a QSE defaults on a Supply Obligation, ERCOT will create a new Obligation for that service in which the QSE defaulted and assign that default Obligation to be equal in MW to the defaulted Supply Obligation.

(2)	If ERCOT opens an Adjustment Period market for the sole reason of resolving a default condition, the QSE’s that are awarded capacity in that Adjustment Period will be paid for their capacity as bid.

(3)	The default Obligation cost will be allocated to those QSE’s who have defaulted on their Obligation for the following Ancillary Services:

(a)	Regulation Up;

(b)	Regulation Down;

(c)	Responsive Reserve; and

(d)	Non-Spinning Reserve.

6.9.2	QSE Obligations for Capacity Services Obtained in the Adjustment Period

6.9.2.1	Settlement for RPRS

The Settlement for RPRS shall be as follows:

6.9.2.1.1	Replacement Reserve Under Scheduled Capacity

(1)	The product of the MCPC multiplied by the amount of capacity insufficiency of each QSE.  The insufficiency for the Operating Hour shall be the sum of:

(a)	The greatest of zero (0) or each difference between the Adjusted Meter Load and the amount of Load scheduled in each Settlement Interval for the Operating Hour at 1300 in the Day Ahead or thirty (30) minutes after ERCOT provides Notice of procurement of RPRS in the Adjustment Period; and

(b)	The greater of zero or the amount of capacity scheduled for the Operating Hour by ERCOT as a result of a mismatch in the QSE’s Schedule as defined in Section 4.7.2, Schedule Validation Process, if any.

(2)	The calculation for Replacement Reserve Service Obligation for underscheduled capacity will be as follows:

USRPizq 	= 	MCPCRPiz * [Max(0,(AMLi1zq – CLi1zq),(AMLi2zq – CLi2zq),(AMLi3zq– CLi3zq),(AMLi4zq– CLi4zq)) + Max(0,(MMSi1zq, MMSi2zq, MMSi3zq, MMSi4zq))]

Where:

i	Interval being calculated.

Note:  intervals 1, 2, 3, and 4 denote a set of intervals in a given hour

z	Zone

USRPiqz	Replacement Reserve Service Under Scheduled Charge ($) for each zone by interval for that QSE

MCPCRPiz	Replacement Reserve Service Market Clearing Price of Capacity ($/MW) per interval per zone.

AMLi1zq	Adjusted Metered Load (MW) per QSE, f, or the first Settlement Interval of the settlement hour, per zone, which will include estimated and/or actual meter values and the associated Transmission Losses & Distribution Losses and UFE.

AMLi2zq	Adjusted Metered Load (MW) per QSE, for the second Settlement Interval of the settlement hour, per zone, which will include estimated and/or actual meter values and the associated Transmission & Distribution Losses and UFE.

AMLi3zq	Adjusted Metered Load (MW) per QSE, for the third Settlement Interval of the settlement hour, per zone, which will include estimated and/or actual meter values and the associated Transmission Losses & Distribution Losses and UFE.

AMLi4zq	Adjusted Metered Load (MW) per QSE, for the fourth Settlement Interval of the settlement hour, per zone, which will include estimated and/or actual meter values and the associated Transmission Losses & Distribution Losses and UFE.

CLi1zq	Current Schedule Load (MW) of that QSE for the first Settlement Interval of the settlement hour, per zone at the time of capacity procurement.

CLi2zq	Current Schedule Load (MW) of that QSE, for the second Settlement Interval of the settlement hour, per zone at the time of capacity procurement.

CLi3zq	Current Schedule Load (MW) of that QSE, for the third Settlement Interval of the settlement hour, per zone at the time of capacity procurement.

CLi4zq	Current Schedule Load (MW) of that QSE, for the fourth Settlement Interval of the settlement hour, per zone at the time of capacity procurement.

MMSi1zq	Mismatched Schedule Quantity (MW) representing Inter-QSE Trades for the first Settlement Interval of the settlement hour per zone per QSE.

MMSi2zq	Mismatched Schedule Quantity (MW) representing Inter-QSE Trades for the second Settlement Interval of the settlement hour per zone per QSE.

MMSi3zq	Mismatched Schedule Quantity (MW) representing Inter-QSE Trades for the third Settlement Interval of the settlement hour per zone per QSE.

MMSi4zq	Mismatched Schedule Quantity (MW) representing Inter-QSE Trades for the fourth Settlement Interval of the settlement hour per zone per QSE.

[PRR613: Replace Section 6.9.2.1.1 with the following upon system implementation.] (1) The product of the MCPC multiplied by the amount of capacity insufficiency of each QSE. The insufficiency for the Operating Hour shall be the sum of: (a) The greatest of zero (0) or each difference between the Adjusted Meter Load and the amount of Load scheduled in each Settlement Interval for the Operating Hour at 1300 in the Day Ahead or thirty (30) minutes after ERCOT provides Notice of procurement of RPRS in the Adjustment Period; and (b) The greater of zero or the amount of capacity that results from either (i) a mismatch in the QSE’s Schedule as defined in Section 4.7.2, Schedule Validation Process, or (ii) a QSE selecting ERCOT as a Resource. (2) The calculation for Replacement Reserve Service Obligation for underscheduled capacity will be as follows: USRPizq=MaxM(MCPCRPMiz)∗ Where, MMQizq=Across qa Where, MMSMi1zqaqb=MAX0, MMSMi2zqaqb=MAX0, MMSMi3zqaqb=MAX0, MMSMi4zqaqb=MAX0,: Where: i Hourly interval being calculated. Note: intervals 1, 2, 3, and 4 denote the set of 15-minute Settlement Intervals in a given hour M Markets, in the event of multiple markets. i.e. Day Ahead versus the Adjustment Periodq QSE qa Buying QSE qb Selling QSE z Zone AMLi1zq Adjusted Metered Load (MW) per QSE, for the first Settlement Interval of the settlement hour, per zone, which will include estimated and/or actual meter values and the associated Transmission Losses & Distribution Losses and UFE. AMLi2zq Adjusted Metered Load (MW) per QSE, for the second Settlement Interval of the settlement hour, per zone, which will include estimated and/or actual meter values and the associated Transmission & Distribution Losses and UFE. AMLi3zq Adjusted Metered Load (MW) per QSE, for the third Settlement Interval of the settlement hour, per zone, which will include estimated and/or actual meter values and the associated Transmission Losses & Distribution Losses and UFE. AMLi4zq Adjusted Metered Load (MW) per QSE, for the fourth Settlement Interval of the settlement hour, per zone, which will include estimated and/or actual meter values and the associated Transmission Losses & Distribution Losses and UFE. CLi1zq Current Schedule Load (MW) of that QSE for the first Settlement Interval of the settlement hour, per zone at the time of capacity procurement. CLi2zq Current Schedule Load (MW) of that QSE, for the second Settlement Interval of the settlement hour, per zone at the time of capacity procurement. CLi3zq Current Schedule Load (MW) of that QSE, for the third Settlement Interval of the settlement hour, per zone at the time of capacity procurement. CLi4zq Current Schedule Load (MW) of that QSE, for the fourth Settlement Interval of the settlement hour, per zone at the time of capacity procurement. MCPCRPMiz Replacement Reserve Service Market Clearing Price of Capacity ($/MW) per hourly interval per zone. MMQizq Mismatched amount (MW) for each zone by hourly interval for that QSE MMSMi1zqaqb Mismatched Schedule Quantity (MW) representing either Inter-QSE Trades, or ERCOT scheduled as a Resource for the first Settlement Interval of the settlement hour per zone per QSE. MMSMi2zqaqb Mismatched Schedule Quantity (MW) representing either Inter-QSE Trades, or ERCOT scheduled as a Resource for the second Settlement Interval of the settlement hour per zone per QSE. MMSMi3zqaqb Mismatched Schedule Quantity (MW) representing either Inter-QSE Trades, or ERCOT scheduled as a Resource for the third Settlement Interval of the settlement hour per zone per QSE. MMSMi4zqaqb Mismatched Schedule Quantity (MW) representing either Inter-QSE Trades, or ERCOT scheduled as a Resource for the fourth Settlement Interval of the settlement hour per zone per QSE. QSSATORPi1 QSE Supply Schedule for the buying QSE, A, for the first Settlement Interval of the settlement hour, at the time of the Replacement Reserve Market. QSSATORPi2 QSE Supply Schedule for buying QSE, A, for the second Settlement Interval of the settlement hour, at the time of the Replacement Reserve Market. QSSATORPi3 QSE Supply Schedule for buying QSE, A, for the third Settlement Interval of the settlement hour, at the time of the Replacement Reserve Market. QSSATORPi4 QSE Supply Schedule for buying QSE, A, for the fourth Settlement Interval of the settlement hour, at the time of the Replacement Reserve Market. QOSBTORPi1 QSE Obligation Schedule for the selling QSE, B, for the first Settlement Interval of the settlement hour, at the time of the Replacement Reserve Market. QOSBTORPi2 QSE Obligation Schedule for the selling QSE, B, for the second Settlement Interval of the settlement hour, at the time of the Replacement Reserve Market. QOSBTORPi3 QSE Obligation Schedule for the selling QSE, B, for the third Settlement Interval of the settlement hour, at the time of the Replacement Reserve Market. QOSBTORPi4 QSE Obligation Schedule for the selling QSE, B, for the fourth Settlement Interval of the settlement hour, at the time of the Replacement Reserve Market. USRPizq Replacement Reserve Service Under Scheduled Charge ($) for each zone by hourly interval for that QSE

6.9.2.1.2	Replacement Reserve Uplift Charge

(1)	Prior to direct assignment of Zonal Congestion costs, the QSE’s Obligation for Replacement Reserve procured for CSC Congestion will be recovered as part of the System Congestion Fund described in Section 7.3.3.1, System Congestion Fund.

(2)	The calculation for Replacement Reserve Uplift Charge will be as follows:

UCRPiq 	= 	-1 * (Σ (PCRPiq + LPCRPiq)q + Σ (USRPiq) +  TCRPAYRPi + Σ (CSCRPiq)q,CSC) * LRSqi

TCRPAYRPi   	= 	-1 * (Σ(TCRcsci ) * SPCSCi )CSC

Where:

i:	Interval being calculated

q:	QSE

z:	CSC zone being settled

UCRPi:	Replacement Reserve Service Uplift Charge ($)

PCRPiQSE	Service Cost ($) per interval for all QSEs of Procured Capacity of Replacement Reserve procured to resolve Zonal Congestion and Capacity Insufficiency per single Resource

LPCRPiQSE	Service Cost ($) per interval for all QSEs of Procured Capacity of Replacement Reserve procured to resolve Local Congestion per single Resource

USRPiQSE	Replacement Reserve Service Under Scheduled Charge ($) per interval for all QSEs

CSCRPiQSE	Replacement Reserve Service CSC Impact Capacity Charge ($) per interval for all QSEs

LRSqi	Load Ratio Share (Factor) (Adjusted Metered Load / Total System Load) per hourly interval of that QSE

TCRPAYRPi	Payment to TCR Account Holders for RPRS market per hourly interval

TCRcsci	Total number of TCRs per CSC per hourly interval

SPCSCi 	Shadow Price of RPRS per CSC per hourly interval

6.9.3	Settlement Charge for VSS

As Generation Entities are not compensated for Voltage Support Service, as specified in Section 6.8.4, Payments for Voltage Support Provided to ERCOT, there is no payment by Load of VSS costs.

[PRR409; upon system implementation, replace Section 6.9.3 with the following.] The cost of Voltage Support Service as specified in Section 6.8.4, Capacity Payments for Voltage Support Provided to ERCOT, will be charged to each QSE on a Load Ratio Share as follows: LAVSSiq = -1*(VARPAYAMTj)*LRSiq

6.9.4	Settlement Obligation for Black Start Service, RMR Standby Service, and RMR Synchronous Condenser Service

(1)	A QSE's Obligation for Black Start Service, RMR Standby Service, and RMR Synchronous Condenser Service will be equal to the QSE’s quantity of energy consumed hourly divided by the sum of all QSE's energy consumed in that hour, multiplied by the total ERCOT hourly cost for each of the following:  Black Start Service, RMR Standby Service, and RMR Synchronous Condenser Service.

6.9.4.1	Settlement Obligations for Black Start Service

(1)	Black Start Service Costs will be allocated on a Load Ratio Share per QSE in the following manner:

LABSqi = -1 * PCBSi * LRSqi

Where:

i	interval, equal to one hour

PCBSi	Procured Capacity ($) for Black Start per interval.

LRSqi 	Load Ratio Share for the QSE per interval

LABSqi 	Black Start Load Charge per interval per QSE.

6.9.4.2	Settlement Obligations for RMR Service

(1)	Reliability Must Run costs, separated by category and available to QSEs via data extract (i.e., Standby Price and energy dollar amounts) will be allocated on a Load Ratio Share per QSE in the following manner:

LARMRiq 	=	-1 * {(Σ (ERMRiq)+ Σ (SBRMRiq) + Σ (UMRMRiq) + ΣERRMRiq) + Σ(CRMRiq)} * LRSiq

Where:

i	Intervalq	QSE

LARMRiq 	RMR Load Allocation for that interval of that QSE

ERMRiq	RMR Energy Dollar Amount per interval of that QSE

SBRMRiq	RMR Standby Price in that interval of the QSE

UMRMRiq	RMR Unexcused Misconduct Fee in that interval of that QSE

LRSiq	Load Share Ratio for that interval of the QSE

ERRMRiq	RMR Energy Rebate Amount for that interval for that QSE

CRMRiq	Payment in that interval to MRA Resources reflecting the equivalent hourly capacity payment* and the actual hourly energy payment to each QSE

*	The equivalent hourly capacity payment for each hour will be determined by dividing each capacity payment by the number of hours covered by the terms of such capacity payment for the term that includes the hour.

6.9.4.3	Settlement Obligations for Synchronous Condenser Service

As Synchronous Condenser Units are not compensated for Synchronous Condenser Service, there is no payment by Load of Synchronous Condenser costs.

[PIP128: No compensation for SC] Synchronous Condenser Costs will be allocated on a Load Ratio Share per QSE in the following manner: SCLAqi = -1 * (Σ (SSBui)u + Σ (SCURMRiu)u + Σ (RunFeeui )u) *LRSiq Where: SCLAqi Synchronous Condenser Load Allocation for that interval SSBui Synchronous Condenser Standby Fee SCURMRiu Start Up Fee RunFeeui Running Fee LRSiq Load Share Ratio for that interval

6.9.5	Settlement Obligation for Balancing Energy Service

6.9.5.1	Balancing Energy Clearing Price

(1)	A Market Clearing Price for Energy (MCPE) will be calculated for each Settlement Interval by Congestion Zone as a product of the mathematical optimization model.  The MCPE will be used to pay or charge each QSE, for each Settlement Interval for Balancing Energy Service.

(2)	In the event there is no Zonal Congestion and all available Balancing Energy Service Up bids are deployed for an interval, ERCOT shall adjust the MCPE as follows:

MCPEa	=	Min (MCPE, 95% price *1.5)

Where:

MCPEa	the adjusted MCPE

MCPE	the unadjusted MCPE

95% price	the MCPE that would result from deploying 95% of the available MW in the Bid Stack

During a Settlement Interval for which an adjusted MCPE is calculated, quantities of Balancing Energy Service Up bids above MCPEa shall be paid as bid, with the sum of incremental payments above the MCPEa charged to each QSE that was charged for Resource Imbalance and/or Load Imbalance during the Settlement Interval, as follows:

IRSiq	=	∑[MAX(0, RIizq) + MAX(0, LIizq)]z/ ∑[(MAX(0, RIizq) + MAX(0, LIizq)]zq

Where:

i	interval being calculated

z	zone being settled

q	QSE

IRSiq	Imbalance Ratio Share per interval per QSE

RIizq	Resource Imbalance ($) per interval per zone by QSE

LIizq	Load Imbalance ($) per interval per zone by QSE

The allocation of charges to QSEs with positive Resource and/or Load Imbalance is:

QPAMiq	=	PAMi * IRSiq

Where:

i	interval being calculated

q	QSE

IRSiq	Imbalance Ratio Share per interval per QSE

QPAMiq	QSE share of incremental payments above the MCPEa

PAMi	Incremental Payments above MCPEa paid out by ERCOT

Incremental payments above MCPEa are uplifted to QSEs that were charged for Load Imbalance and Resource Imbalance for intervals in which an adjusted MCPE is calculated.

The incremental amount paid above MCPEa will be calculated manually by truncating the aggregate Bid Stack at the MCPEa level and determining how many MW were accepted above this amount.  The integrated MWh under the curve will be paid as bid.  The total incremental amount will be uplifted to QSEs through the method described above.

6.9.5.2	Settlement For Balancing Energy for Load Imbalances

(1)	For each applicable Congestion Zone and each Settlement Interval, each QSE’s charge or credit for Balancing Energy consumed or provided in the Congestion Zone during the Settlement Interval, shall equal the sum of:  1) the product of the Congestion Zone’s MCPE and the QSE’s Balancing Energy Obligation for that Congestion Zone for Resources; and 2) the product of the Congestion Zone’s MCPE and the QSE’s Balancing Energy Obligation for that Congestion Zone for Obligations.

(2)	Each QSE’s Resource Balancing Energy Obligation (in MWh) for each Resource for each Settlement Interval, for each Zone, shall be equal to the actual energy production of all Resources represented by the QSE during the Settlement Interval; minus the QSE’s final Balanced Schedule of its Resources for that Congestion Zone less any Inter-QSE Trades scheduled as a Resource.  This cost will be calculated as Resource Imbalance as indicated in Section 6.8.1.13, Resource Imbalance.

(3)	Each QSE’s Load Balancing Energy Obligation quantity for each Settlement Interval, for each Zone, shall be equal to the QSE’s Adjusted Metered Load consumption of all CR Loads represented by the QSE, minus the QSE’s scheduled Load Obligation (total Obligation less any Inter-QSE Trades scheduled as a Load Obligation) for that Congestion Zone.  This Load Imbalance will be calculated as follows:

LIizq 	= 	-1 * (SLizq – AMLizq) * MCPEiz

LIiz 	= 	SUM(LIizq)q

Where:

i	interval being calculated

z	zone being settled

LIizq	Load Imbalance ($) per interval per zone per QSE

SLizq	Scheduled Load (MWh) per interval per zone per QSE (total Obligation – Inter-QSE Trades)

AMLizq	Adjusted Metered Load (MWh) per interval per zone per QSE, which will include estimated and/or actual values and the associated Transmission & Distribution Losses and UFE.

MCPEiz	Market Clearing Price of Energy ($/MWh) per interval per zone

(4)	The QSE will pay the following for Load Imbalance if the net amount is positive.  If the net amount is negative, the QSE will receive payment from the ERCOT in accordance with the Visa settlement sign conventions.

(5)	Load Imbalance does include scheduled Exports from a DC Tie.

(6)	Each QSE’s Adjusted Metered Load in a Congestion Zone during a Settlement Interval shall be adjusted for Unaccounted for Energy (UFE), Transmission Losses and Distribution Losses, as per Section 13, Transmission and Distribution Losses determined by ERCOT in accordance with Section 11, Data Acquisition and Aggregation.

6.9.6	Settlement for Capacity Payments for Balancing Energy Up Load

Capacity payments made for Balancing Up Loads deployments will be allocated on a Load Ratio Share per QSE by summing the payments made for Balancing Up Loads capacity in each interval and multiplying it by the Load Ratio Share for that interval of the given QSE.  The charge allocation will be calculated as follows:

LABULqi 	= 	-1 * PCBULi * LRSqi

Where:

i	interval

q:	QSE

PCBULi 	Sum of any paid capacity ($) for Balancing Energy Up on Loads per interval

LRSqi 	Load Ratio Share for the QSE per interval

LABULCqi 	Balancing Energy Up capacity Load allocation charge per interval per QSE

6.9.7	Settlement Obligations for Premiums for Individual Resource Dispatch Payments

Premiums paid for managing Local Congestion will be shared by the QSE’s Load Ratio Share for the hours during which the premiums were paid.

6.9.7.1	OOM Capacity Charge

(1)	The cost of Replacement Capacity that is not assigned in the mathematical optimization process will be shared by all QSEs in relation to their Load Ratio Share of the total ERCOT Load for the interval.  The OOM Replacement Capacity Load Allocation will be calculated as follows:

LAOOMRPqi	=	-1 * PCOOMRPi *  LRSqi

Where:

i 	interval

u 	unit

z	zone

LAOOMqi	OOM Replacement Capacity Load Allocation Charges ($) for that QSE in that interval

PCOOMRPi	OOM Replacement Capacity Costs ($) for the total market for that interval

LRSqi	Load Ratio Share (0-1) = (Adjusted Metered Load for that QSE per interval/ Total System Load per interval)

6.9.7.2	OOM Energy Charge

(1)	Out Of Merit (OOM) Energy Load and Zonal OOME Load will be allocated on a Load Ratio Share per QSE by taking the sum of OOME and Zonal OOME Costs of all zones in that interval and multiplying it by the Load Ratio Share for that interval of the given QSE.  The OOM Energy Load Allocation will be calculated as follows:

ELAoomiq 	=	-1 *  Σ (EOOMUPiz + EOOMDNiz)z   * LRSiq

Where:

i	interval

u	unit

z	zone

ELAOOMiq	OOM Energy and Zonal OOME Charges per interval per QSE

LRSiq	Load Ratio Share Factor (0-1) = (Adjusted Metered Load for that QSE per interval / Total System Load for that interval for that QSE

LRSiq = AMLiq / AMLi

EOOMUPiz	Out of Merit Energy and Zonal OOME Up Payments per interval per zone

EOOMDNiz	Out of Merit Energy Down and Zonal OOME Down Payments per interval per zone

6.9.8	Settlement for Mismatched Inter-QSE Energy Schedules

QSE’s will be paid the MCPE multiplied by the mismatch amount delivered to ERCOT and will be charged the MCPE multiplied by the mismatch amount received from ERCOT.

The mismatch amount delivered to ERCOT for each QSE for each zone shall be the entire amount in the mismatched inter-QSE energy schedules submitted by the QSE as a Resource.  The mismatch amount received from ERCOT for each QSE for each zone shall be the entire amount in the mismatched inter-QSE energy schedules submitted by the QSE as a Load.

[PRR548: Replace the above paragraph with the following upon system implementation:] The mismatch amount delivered to ERCOT for each QSE for each zone shall be any amount in the mismatched inter-QSE energy schedules submitted by the QSE as a Resource which exceeds the corresponding Inter-QSE energy schedule submitted by a QSE as a Load. The mismatch amount received from ERCOT for each QSE for each zone shall be any amount in the mismatched inter-QSE energy schedules submitted by the QSE as a Load which exceeds the corresponding Inter-QSE energy schedule submitted by a QSE as a Resource.

MISDiqz  	= 	-1 * MISAMTDiqz * MCPEiz

MISRiqz 	= 	MISAMTRiqz * MCPEiz

Where:

i	interval

q	QSE

z	zone

MISDiqz	Mismatched schedule payment for the mismatched amount delivered to ERCOT, per interval, per QSE, and per zone.

MISRiqz	Mismatched schedule charge for the mismatched amount received from ERCOT, per interval, per QSE, and per zone.

MISAMTDiqz	Mismatched amount delivered to ERCOT due to mismatched schedule per interval, per QSE, and per zone.

MISAMTRiqz	Mismatched amount received from ERCOT due to mismatched schedule per interval, per QSE, and per zone.

MCPEiz	Market Clearing Price for Energy per interval, and per zone.

Also:

MISDiz 	= 	Σ (MISDiqz)q

MISRiz 	= 	Σ (MISRiqz)q

Where:

MISDiz	Total mismatched schedule payments for the mismatched amounts delivered to ERCOT, per interval, and per zone.

MISRiz	Total mismatched schedule charges for the mismatched amounts received from ERCOT, per interval, and per zone.

6.10	Ancillary Service Qualification, Testing and Performance Standards

6.10.1	Introduction

QSEs providing Ancillary Services shall meet qualification criteria and performance measures to operate satisfactorily with ERCOT.  ERCOT shall develop an Ancillary Services qualification and testing program and Real Time Monitoring Program for all suppliers of Ancillary Services that is based on the key factors needed for reliability.  These programs will be approved by ERCOT Technical Advisory Committee and will be included in the Operating Guides.  These performance factors shall be measured as precisely and efficiently as possible.  General capacity testing verifies a Generation Resources or Load acting as Resources and Net Dependable Capability.  Qualification tests allow the potential provider’s portfolio to demonstrate the minimum capabilities necessary to deploy an Ancillary Service, and performance measures assess the Real Time delivery of a service by an Ancillary Services provider.

All loads may be provisionally qualified for a period of ninety days as a Load acting as a Resource and may be eligible to participate as Resource.  Loads that have installed the appropriate equipment with verifiable testing data may be provisionally qualified as a provider of Ancillary Services once the specific requirements for the Ancillary Services specified in the Operating Guides have been completed to ERCOT’s reasonable satisfaction.

All loads may be provisionally qualified for a period of ninety (90) days to participate as a Balancing Up Load (BUL), provided the Load is metered with an IDR to ERCOT’s reasonable satisfaction.  Any Load may be qualified to participate as a BUL Resource, provided the Load meets the metering requirements (including any Sampling standards identified in Section 18, Load Profiling) established by ERCOT once the following ERCOT requirements have been met:

- ESI-ID registration of BUL by the QSE;

- Telemetered BUL response value is installed and tested between QSE and ERCOT; and

- For Dynamic Obligation Schedule (DSBUL), telemetered dynamic Obligation telemetry tested between QSE and ERCOT.

Provisional qualification as described herein may be revoked by ERCOT at any time for any non-compliance with provisional qualification requirements.

6.10.2	General Capacity Testing Requirements

QSEs shall provide ERCOT a list identifying each Generation Resource unit that is expected to operate more than one hundred sixty eight (168) hours in a Season as a provider of energy and/or Ancillary Services.  ERCOT shall evaluate, during each Season of expected operation, the Net Dependable Capability of each unit expected to operate more than one hundred sixty eight (168) hours during that season, except for any Generation Resources used solely for energy services and whose capacity is less than ten (10) MW.  Prior to the beginning of each Season, QSEs shall identify the Generation Resources to be tested during the Season and the specific week of the test if known.  This schedule may be modified by the QSE (including retests) during the Season.  QSEs not identifying a specific week for a Generation Resource unit test must test the unit within the first one hundred sixty eight (168) hours of run time during the Season or operate with a Net Dependable Capability equal to the highest integrated hourly MWh output demonstrated during the first one hundred sixty eight (168) hours of run time.  QSEs do not have to bring units On-line or shut down solely for the purpose of the seasonal verification.  Any unit for which the QSE desires qualification to provide Ancillary Services shall have its Net Dependable Capability verified prior to providing services using the Generation Resource unit even if it fits the less than one hundred sixty eight (168) hour or small capacity exception.  The capability of hydro units operating in the synchronous condenser fast response mode to provide hydro Responsive Reserve shall be evaluated by Season.

Load acting as a Resource to provide Ancillary Services shall have its telemetry attributes verified by ERCOT annually.  In addition, once every two (2) years, any LaaR providing Responsive Reserve Service shall test the under frequency relay or the output from the solid-state switch, whichever applies, for correct operation.  However, if the Load’s performance has been verified through response to an actual event, the data from the event can be used to meet the annual telemetry verification requirement for that year and/or the biennial relay testing requirement.

Specific Loads to be used for the first time as a Resource to provide Responsive Reserve, Non-Spinning Reserve or Replacement Reserve must be correctly evaluated (tripped or simulated trip, if approved by ERCOT) prior to their qualification to provide Ancillary Services.  At a time selected mutually by the Load and ERCOT, ERCOT will notify the QSE representing such Load of the need to confirm that Loads proposed to be used to provide Responsive Reserve, Non-Spinning Reserve or Replacement Reserve Services can be de-energized, or simulated, if applicable, to ERCOT’s reasonable satisfaction.  ERCOT shall develop a standard test for simulation for Load interruption required under this subsection.  Loads used to provide Responsive Reserve Service shall be qualified for correct operation by their host TDSP.

QSEs shall be responsible for qualifying any Load desiring to have the QSE represent it to provide Balancing Up Load (BUL) Service.

[PRR484: Add the following to the end of the above paragraph (“QSEs shall be responsible for qualifying…Balancing Up Load (BUL) Service. ”) upon system implementation:] Loads controlled under a qualified DLC program may be qualified as a group.

The QSE shall nominate to ERCOT, at least annually, that it is representing an amount of BUL for which it wishes to be qualified to provide.  At a time selected by ERCOT, the ERCOT operator will notify the QSE that it wants to verify the QSE’s ability to provide ERCOT with the appropriate signal simulating that it has initiated an ERCOT requested BUL reduction.  The QSE Operator will immediately simulate the initiation of the reduction and provide ERCOT with the appropriate signal representing some amount of Load to be qualified to provide BUL Resources.  Once ERCOT has verified that it has received an appropriate Load reduction signal from the QSE and has successfully completed the BUL registration process, the QSE will be qualified to provide BUL Resources.  Any changes to the BUL portfolio will require subsequent updates to the registration process.  For NOIEs representing specific Loads qualified as BULs that are located behind the NOIE Settlement Meter points, the NOIE shall provide an alternative unique descriptor of the qualified BUL Load for ERCOT’s records.

Generation Resources and Loads acting as Resources shall be evaluated at least annually by ERCOT for:

(1)	Correct operation of telemetry of the breakers controlling the Resource;

(2)	Correct mapping of QSE-provided telemetry of Ancillary Service energy to the appropriate energy Settlement Meter;

(3)	Data rate update requirements; and

(4)	Any other required telemetry attributes.

All Generation Resources and Loads acting as a Resource shall meet all requirements specified in the Operating Guides for proper response to system frequency.  ERCOT may reduce the amount a Resource may contribute toward Ancillary Services if it finds unsatisfactory performance of the Resource as defined in these Protocols and the Operating Guides.

Qualification of a Resource, including a Load acting as a Resource, shall remain valid for such Resource in the event of a change of QSE for the Resource, provided that the new QSE demonstrates to ERCOT’s reasonable satisfaction that the new QSE has adequate communications and control capability for the Resource.

6.10.3	Ancillary Services Qualification Criteria and Portfolio Test Methods

Only QSEs that have been qualified and tested may be used to provide Ancillary Services.  ERCOT shall develop and operate its qualification and testing program to meet the following requirements for each Ancillary Service.

A QSE shall be qualified and tested to provide Service prior to initial operation and every five years thereafter.

A QSE may request a test for re-qualification at any time, but no later than the expiration of its current Ancillary Service qualification, and no more frequently than once every twelve (12) months.  At the time of a request by a QSE for re-qualification, ERCOT may approve the re-qualification based on the AS performance metrics using the following criteria:

(1)	For Balancing Energy and RGS, the QSE’s SCE Monitoring Criteria performance scores in Section 6.10.5.3, SCE Monitoring Criteria, were passing for five (5) out of the previous six (6) months.

(2)	For RRS, the RRS criteria in Section 6.10.5.4, Responsive Reserve Services Performance Monitoring Criteria, were passing for five (5) out of the previous six (6) deployment measurements.

(3)	For NSRS, the NSRS monitoring criteria in Section 6.10.5.5, Non-Spinning Reserve Services Performance Monitoring Criteria, were passing for five (5) out of the previous six (6) deployment measurements without retest.

If the QSE passes the criteria, the QSE will be exempt from re-qualification testing for five (5) years from the date of the exemption request.  ERCOT shall provide monthly performance updates to the QSE for the above criteria.

ERCOT is authorized to call up to two unannounced, unscheduled qualification tests after presenting to the QSE supporting information of an indication that a Resource may not be able to meet its stated Net Dependable Capability during any calendar year.

QSEs may qualify by using either Generation Resource(s) or Load(s) Acting as a Resource (LaaR(s)).  If a QSE qualifies by using only a LaaR then the QSE may only provide Ancillary Services using LaaRs and will not be qualified to provide Ancillary Services using Generation Resources.  However, if a QSE successfully completes the qualification using Generation Resource(s), that QSE will be qualified to provide Ancillary Services from both Generation Resources and LaaRs.

ERCOT may grant a “Provisional Qualification,” for a period not to exceed ninety (90) days, to a QSE that has performed an Ancillary Service qualification test (or tests) in good faith but failed to qualify due to problems that, in the sole discretion of ERCOT, are determined to be non-critical for the purpose of providing one or more Ancillary Services.  Notwithstanding the failure of a QSE with Provisional Qualification to meet the applicable Ancillary Service criteria, such QSE may provide such Ancillary Service to the extent permitted by the terms of the Provisional Qualification.

6.10.3.1	Regulation

(1)	A regulation qualification test is conducted during a continuous sixty (60) minute period agreed on in advance by the QSE and ERCOT.  QSEs may be qualified to provide Regulation Up or Regulation Down, or both, in separate testing.

(2)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice communication circuits in order to validate the voice circuits.

(3)	For the sixty (60) minute duration of the test, when market and reliability conditions allow, the ERCOT Control Area Operator shall send a random sequence of raise, hold, and lower control signals to the QSE, To facilitate accurate measurements, each signal (raise, lower, or hold) shall remain unchanged for at least two (2) minutes.  The control signals shall not request QSE portfolio performance beyond the stated high limit, low limit, and ramp rate limit agreed on prior to the test.  During the test, one ten (10) minute period will test the QSE’s ability to achieve the entire amount of Regulation Up requested for qualification during the period.  One ten (10) minute period will test the QSE’s ability to achieve the entire amount of Regulation Down requested for qualification during the period.  To facilitate testing of large portfolios, ERCOT may test maximum ramp capability on subsets of Generation Resources in a portfolio.

(4)	The QSE’s portfolio average real power output for each clock minute will be measured and recorded.  The regulation test shall be conducted when all other schedules are held constant so that any real power increase or decrease is the result of the regulation requirement.  The correlation coefficient between the expected average power from one minute to the next [limited to no more than the initial value + (request ´ 1/2 ´ stated ramp rate)], and the actual measured real power output during those minutes shall be statistically significant to two (2) positive standard deviations in order to pass the test.

(5)	On successful demonstration of all test criteria, ERCOT shall qualify the QSE is capable of providing RGRS and shall provide a copy of the certificate to the QSE.

6.10.3.2	Responsive Reserve Qualification Testing Criteria

(1)	Testing using Generation Resource(s)

(a)	A test for RRS shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow, and not previously disclosed to the QSE, ERCOT shall send a signal to the QSE requesting it to provide an amount of RRS.  The QSE shall acknowledge the start of the test.

(d)	For the thirty (30) minute duration of the test, the QSE output shall be measured as clock-minute average outputs for:  (i) the clock-minute prior to the instructions being received from ERCOT; (ii) the clock-minute following receipt of instructions from ERCOT and continuing for ten (10) minutes; and (iii) for each of the subsequent nineteen (19) clock-minutes.  All measurements shall confirm the additional delivery of energy due to the deployment of Responsive Reserve Service in an amount equal to at least ninety-five percent (95%) and no more than one hundred five percent (105%) of the amount requested by ERCOT.  Satisfactory performance shall be deemed acceptable if ninety percent (90%) of each clock-minute measurement ten (10) minutes after notice through the balance of the test period is equal to at least ninety-five percent (95%) and no more than one hundred five percent (105%) of the amount expected.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify that the QSE is capable of providing RRS and shall provide a copy of the certificate to the QSE.

(2)	Testing using Load(s) Acting as a Resource

(a)	A test for RRS shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow, and not previously disclosed to the QSE, ERCOT shall send a signal to the QSE requesting it to provide an amount of RRS.  The QSE shall acknowledge the start of the test.

(d)	Upon ERCOT issuing a verbal instruction to the QSE to deploy the LaaR, the QSE shall demonstrate that it has procedures in place to satisfy a satisfactory deployment of the LaaR(s) providing Responsive Reserve Service as required in Step 2 of an EECP, Protocol Section 5.6.7, EECP STEPS, Step 2 (2).  All measurements shall confirm the additional delivery of energy due to the deployment of Responsive Reserve Service in an amount equal to at least ninety-five percent (95%) and no more than one hundred and fifty percent (150%) of the amount requested by ERCOT.  A deployment will be deemed acceptable when ERCOT confirms the interruption of the Load(s) within ten (10) minutes of issuance of the instruction by ERCOT.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify that the QSE is capable of providing RRS from LaaRs and shall provide a copy of the certificate to the QSE designating its qualification to provide RRS from LaaRs.

6.10.3.3	Non-Spinning Reserve Qualification Testing Criteria

(1)	Testing using Generation Resource(s)

(a)	A test for Non-Spinning Reserve Service shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow and not previously disclosed to the QSE, ERCOT shall notify the QSE using ERCOT’s Messaging System requesting it to provide an amount of Non-Spinning Reserve the QSE wishes to be qualified to.  The QSE shall acknowledge the start of the test.

(d)	For the sixty (60) minute duration of the test, the QSE output shall be measured as clock-minute average outputs for:  (i) the clock-minute prior to the instructions being received from ERCOT; (ii) the clock-minute following receipt of instructions from ERCOT and continuing for thirty (30) minutes; and (iii) for each of the subsequent twenty-nine (29) clock minutes.  All measurements shall confirm the additional delivery of energy due to the deployment of Non-Spinning Reserve Service in an amount equal to at least ninety-five percent (95%) and no more than one hundred five percent (105%) of the amount requested by ERCOT.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify the QSE is capable of providing Non-Spinning Reserve and shall provide a copy of the certificate to the QSE.

(2)	Testing using Load(s) Acting as a Resource

(a)	A test for Non-Spinning Reserve Service shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow, and not previously disclosed to the QSE, ERCOT shall notify the QSE using ERCOT’s Messaging System requesting the QSE provide the amount of Non-Spinning Reserve the QSE wishes to be qualified to provide.  The QSE shall acknowledge the start of the test.

(d)	Upon ERCOT issuing a verbal instruction to QSE to deploy the LaaR, the QSE shall demonstrate that it has procedures in place to satisfactorily deploy LaaR(s) providing Non-Spinning Reserve Service. All measurements shall confirm the additional delivery of energy due to the deployment of Non-Spinning Reserve Service in an amount equal to at least ninety-five percent (95%) and no more than one hundred and fifty percent (150%) of the amount requested by ERCOT.  A deployment will be deemed acceptable when ERCOT confirms the interruption of the Load(s) within thirty (30) minutes of issuance of the instruction by ERCOT.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify that the QSE is capable of providing Non-Spinning Reserve from LaaRs and shall provide a copy of the certificate to the QSE designating its qualification to provide Non-Spinning Reserve from LaaRs.

6.10.3.4	Balancing Energy

(1)	Testing using Generation Resource(s)

(a)	A test for Balancing Energy Service shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow and not previously disclosed to the QSE, ERCOT shall notify the QSE using ERCOT’s Messaging System requesting it to provide an amount of Balancing Energy.  The QSE shall acknowledge the start of the test.  During the sixty (60) minute duration of the test, within the limits of requested qualification, ERCOT will vary the amount of Balancing Energy requested.

(d)	A QSE may qualify to provide only Balancing Energy Down Service using only Uncontrollable Renewable Resources by providing Balancing Energy Down Service, within the limits of requested qualification, in an amount available from the Uncontrollable Renewable Resource’s Resource Plan at the time of the Dispatch Instruction.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify the QSE is capable of providing Balancing Energy and shall provide a copy of the certificate to the QSE.

(2)	Testing using Load(s) Acting as a Resource

(a)	A test for Balancing Energy Service shall be performed during a continuous eight (8) hour window agreed on by the QSE and ERCOT.

(b)	ERCOT shall confirm the date and time of the test with the QSE using both the primary and alternate voice circuits to validate the voice circuits.

(c)	At any time during the window, selected by ERCOT when market and reliability conditions allow, and not previously disclosed to the QSE, ERCOT shall notify the QSE using ERCOT’s Messaging System requesting it to provide an amount of Balancing Energy.  The QSE shall acknowledge the start of the test.

(d)	Upon ERCOT issuing a verbal instruction to QSE to deploy the LaaR, the QSE shall demonstrate that it has procedures in place to satisfactorily deploy LaaR(s) providing Balancing Up Energy Service. All measurements shall confirm the additional delivery of energy due to the deployment of Balancing Up Energy Service in an amount equal to at least ninety-five percent (95%) and no more than one hundred and fifty percent (150%) of the amount requested by ERCOT.  A deployment will be deemed acceptable when ERCOT confirms the interruption of the Load(s) within ten (10) minutes of issuance of the instruction by ERCOT.

(e)	On successful demonstration of all test criteria, ERCOT shall qualify that the QSE is capable of providing Balancing Energy from LaaRs and shall provide a copy of the certificate to the QSE designating its qualification to provide Balancing Energy from LaaRs.

6.10.3.5	Reactive Supply from Generation Resources required to provide VSS

(1)	The Generation Entity must verify and maintain its stated Reactive Power capability for each of its Generation Resources required to provide VSS, as required by the Operating Guides.  Generation Resources required to provide VSS reactive capability limits shall be specified considering nominal substation voltage.

(2)	The Generation Entity will conduct reactive capacity qualification tests to verify the maximum leading and lagging reactive capability of all Generation Resources required to provide VSS.  Reactive  capability tests will be performed on initial qualification and at a minimum of once every two years ERCOT may require additional testing if it has information indicating that current data is inaccurate.  The Generation Entity is not obligated to place Generation Resources required to provide VSS On-line solely for testing.  The reactive capability tests are run at a time agreed on in advance by the Generation Entity, its QSE, the applicable TDSP, and ERCOT.

(3)	Maximum lagging power factor reactive operating limit shall be demonstrated during peak Load Season, at or above ninety-five percent (95%) of the most currently tested net dependable megawatt capability, insofar as system voltage conditions and other factors will allow.  The Generation Resource required to provide VSS should be required to maintain this level of Reactive Power for at least fifteen (15) minutes.

(4)	Maximum leading power factor reactive operating limit shall be demonstrated during light Load conditions, with the unit operating at a typical output for that condition, insofar as system voltage conditions and other factors will allow.  The unit should be required to maintain this level of Reactive Power for at least fifteen (15) minutes.

(5)	The Generation Entity shall perform the unit Automatic Voltage Regulator (AVR) tests and shall supply AVR data as specified in the Operating Guides.  The AVR tests will be performed on initial qualification and periodically at an ERCOT-set interval no more often than once every five (5) years.  The AVR tests are run at a time agreed on in advance by the Generation Entity, its QSE, the applicable TDSP, and ERCOT.

6.10.3.6	System Black Start Capability

(1)	Qualification will be provided to any Black Start Resource that has met the following requirements:

(a)	Verified control communication path performance;

(b)	Verified primary and alternate voice circuits for receipt of instructions;

(c)	Passed the basic starting test;

(d)	Passed the line energizing test;

(e)	Passed the Load carrying test;

(f)	Has started the next start unit, or has started the next start unit’s largest required motor and satisfied the next start unit’s minimum startup Load requirements; or has been demonstrated to the satisfaction of ERCOT staff through simulation studies conducted by the Black Start Service provider or a qualified third party, to be capable of starting the next start unit’s largest required motor while meeting the next start unit’s minimum startup Load requirements.  Potential Black Start Service bidders may request next start unit information from ERCOT prior to the selection process to satisfy this requirement.  ERCOT shall require this information from the designated next start unit as follows:  ERCOT may require any Generation Resource to provide largest motor startup information and unit startup energy requirements as needed to validate Black Start proposals or plans submitted by other Generation Resources.  Such data, if requested by ERCOT, shall be provided by the QSE representing the Generation Resource, or the Generation Resource Entity to ERCOT within thirty (30) days or less;

(g)	If not starting itself, has an ERCOT approved firm standby power contract with deliverability under ERCOT blackout circumstances from another power pool that can be finalized upon selection as a Black Start Resource;

(h)	If not starting itself, has an ERCOT approved agreement with the necessary TDSPs for access to another power pool, for coordination of switching during a Black Start event, for coordination of maintenance through the ERCOT Outage scheduler for all non-redundant transmission startup feeds; and

(i)	If dependent upon non-ERCOT transmission Resources, agreements providing this Transmission Service have been provided in the proposal.

(2)	On successful demonstration of system Black Start Service capability, ERCOT shall qualify the Black Start Resource as being permitted to provide the system Black Start Service capacity and shall provide a copy of the certificate to the Black Start Resource.  Qualification shall be valid for one year from the date of the last successful Basic Starting test, three years from the date of the last successful line energizing test, or six (6) years from the date of the last successful Load carrying test, whichever is earliest.  Qualification shall be revoked if the Black Start Resource fails to perform successfully during an actual restoration event, until the Black Start Resource is successfully retested.  Retesting is only required for the aspect of system Black Start Service capability (basic starting, line energizing, or Load carrying) for which the Black Start Resource failed.

(a)	Basic Starting Test:

(i)	The basic ability of the Black Start Resource to start itself, or start from a normally open interconnection to another power pool, without support from the ERCOT System, is tested annually, either as a stand-alone test or part of the line energizing and Load carrying tests.  The test is run during a one-week period agreed on in advance by the Black Start Resource and ERCOT and must not cause Outage to ERCOT Customer Load or the availability of other Resources to the ERCOT market;

(ii)	ERCOT shall confirm the dates of the test with the Black Start Resource;

(iii)	At a time during a previously agreed test week window not previously disclosed to the Black Start Resource, ERCOT will initiate the test;

(iv)	The Black Start Resource, including all auxiliary Loads, will be isolated from the ERCOT power system, except for the transmission that connects the Resource to another power pool if the startup power is supplied by a firm standby contract.  Black Start Resources starting with the assistance of another power pool through a firm standby agreement will connect to the external grid, start-up, carry internal Load, disconnect from the external grid if not supplied through a black start capable DC Tie, and continue equivalently to what is required of other Black Start units;

(v)	The Black Start Resource will start without assistance from the ERCOT System, except for the transmission that connects the Resource to another power pool if the startup power is supplied by a firm standby contract;

(vi)	The Black Start Resource must remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or Loads in the immediate area for at least thirty (30) minutes; and

(vii)	The Black Start Resource must have verified that its Volts/Hz relay, over excitation limiter, and under excitation limiter are set properly and that no protection devices will trip the unit within the required reactive range.  Data to verify these settings will be provided to ERCOT.

(b)	Line Energizing Test:

(i)	The ability of the Black Start Resource to energize transmission will be tested when conditions permit as determined by the TDSP but at least once every three years.  Tests will be conducted at a time agreed on by the Black Start Resource, TDSP, and ERCOT:

(ii)	Sufficient transmission will be de-energized such that when it is energized by the Black Start Resource it demonstrates the Black Start Resource’s ability to energize enough transmission to deliver to the Loads the Resource’s output that ERCOT’s restoration plan calls for the Black Start Resource to supply.  ERCOT shall be responsible for transmission connections and operations that are compatible with the capabilities of the Black Start Resource;

(iii)	Conduct a Basic Starting Test;

(iv)	ERCOT will direct the Black Start Resource to energize the previously de-energized transmission, while monitoring frequency and voltages at both ends of the line.  Alternatively, if ERCOT agrees, the transmission line can be connected to the Black Start Resource before starting, allowing the Resource to energize the line as it comes up to speed; and

(v)	The Black Start Resource must remain stable (in both frequency and voltage) while supplying only its own auxiliary Loads or external Loads and controlling voltage for at least thirty (30) minutes.

(c)	Load Carrying Test:

(i)	The ability of the Black Start Resource to remain stable and to control voltage and frequency while supplying restoration power to the Load that ERCOT’s restoration plan calls for the Black Start Resource to supply shall be tested as conditions permit, but at least once (1) every six (6) years;

(ii)	Conduct a Basic Starting Test;

(iii)	Conduct a line energizing test; and

(iv)	The TDSP operator will direct picking up sufficient Load to demonstrate the Black Start Resource’s capability to supply the required power identified in ERCOT’s restoration plan, while maintaining voltage and frequency for at least thirty (30) minutes.

(3)	Qualification shall be revoked for that calendar year if the Black Start Resource fails to perform successfully during an actual ERCOT System black out event and the unit has been declared available, as defined in Section 9B(1) of the “Standard Form Black Start Agreement.”

6.10.4	Ancillary Service Deployment Performance Measures

ERCOT shall measure the performance of QSEs according to the following requirements.  ERCOT shall identify those QSEs that continually perform at a less-than-satisfactory level and shall pursue compliance mechanisms for QSEs as specified in the NERC Reliability Compliance Program and as may be further specified in the Protocols and Operating Guides.

6.10.4.1	Performance Measurement Standard

The expected amount of energy resulting from the deployment instructions of ERCOT is represented as a real power schedule of instructed Ancillary Services from the QSE.  This schedule, subject to the agreed-on QSE capabilities, is the requested Ancillary Service output of the QSE Resources.  Considering that the QSE may be operating a portfolio and has scheduled a base energy quantity for each Settlement Interval, the total QSE schedule is the amount of power from the base Resource schedule plus any such instructed Ancillary Services.  The performance of a QSE can be measured by the difference between the actual and expected (requested) Resource output of the QSE.  The ERCOT Ancillary Services that result in the deployment of real power applies in the measurement of Real Time provision of the reliability product are (1) Regulation Service, (2) Responsive Reserve Service, (3) Non-Spinning Reserve Service, and (4) Balancing Energy Service.  These services combined form ERCOT Reliability Ancillary Services.

Performance measures for the remaining Ancillary Services, Replacement Reserves, Reactive Power Supply from Generation and System Black Start are treated separately.

6.10.4.2	Base Power Schedule Calculation.

For performance measurement purposes, ERCOT shall calculate for each QSE every two (2) seconds the expected power resulting from the QSE’s Resource schedule less any other QSEs scheduled as a Resource.  The expected power function will be calculated such that schedule changes between Settlement Intervals will be ramped during a ten (10) minute fixed ramp period starting five (5) minutes prior to the start of a Settlement Interval.  ERCOT will consider energy provided outside of the Resource schedule in the Settlement Interval as a result of ramping an instructed deviation.

[PRR601: replace the paragraph above with the following upon system implementation:] For performance measurement purposes, ERCOT shall calculate for each QSE every two (2) seconds the expected power resulting from the QSE’s Resource schedule less any other QSEs scheduled as a Resource. The expected power function will be calculated such that schedule changes between Settlement Intervals will be ramped during a fifteen (15) minute fixed ramp period starting seven and-a-half (7.5) minutes prior to the start of a Settlement Interval. ERCOT will consider energy provided outside of the Resource schedule in the Settlement Interval as a result of ramping an instructed deviation.

6.10.4.3	Balancing Energy Power Schedule

For performance measurement purposes, ERCOT shall calculate for each QSE the Balancing Energy power schedule for the expected power resulting from the change in deployment of Balancing Energy Service.  The Balancing Energy power schedule will ramp to the new deployment level during a fixed ramp period starting five (5) minutes prior to the target service interval and ending five (5) minutes after the start of the target service interval.

6.10.4.4	Schedule Control Error

ERCOT will calculate the following for each QSE for each two-second period:

SCE	=	Actual Generation

+	Load Resource Response to Instructions

–	Base Power Schedule

–	Sum of any Dynamic Resource Power Schedules

–	Expected Governor Response due to frequency of the QSE’s portfolio of Resources

–	Instructed Ancillary Services power

–	The signal sent to ERCOT that is estimated in Real Time representing the real power interrupted in response to the deployment of Balancing Up Load (BUL) for Dynamically Scheduled Load

–	Fleet/Zonal OOME Dispatch Instruction

[PRR307: Revise Section 6.10.4.4 as follows when system change implemented.] 6.10.4.4 Schedule Control Error ERCOT will calculate the following for each QSE for each two-second period: SCE = Actual Generation + Load Resource Response to Instructions – Base Power Schedule – Sum of any Dynamic Resource Power Schedules – Expected Automatic Response due to frequency of the QSE’s portfolio of Resources – Instructed Ancillary Services power – The signal sent to ERCOT that is estimated in Real Time representing the real power interrupted in response to the deployment of Balancing Up Load (BUL) for Dynamically Scheduled Load – Fleet/Zonal OOME Dispatch Instruction

Instructed Ancillary Services 	=	Instructed (Regulation Service

+	Responsive Reserve

+	Non-Spinning Reserve

+	Balancing Energy power schedule)

LaaR response to Instructions is provided for each interruptible LaaR that is indicated available in the Resource Plan according to the following formula:

LaaR response to Instructions = ∑ per LaaR (last telemetered breaker load MW value prior to deployment - current telemetered breaker load MW value)

6.10.5	QSE Real Power Performance Criteria

6.10.5.1	Base Power Schedule Monitoring Criteria

QSEs shall make their Resources operate to the final Resource bilateral schedules as converted to a base power function according to the method specified in Section 6.10.4.2, Base Power Schedule Calculation, except as noted in Section 6.10.6.  Measurement of performance shall be accomplished using the SCE monitoring criteria described in Section 6.10.5.3, SCE Monitoring Criteria.

6.10.5.2	Balancing Energy Performance Monitoring Criteria

QSEs providing only Balancing Energy Services shall declare this intent to ERCOT in the Scheduling Process.  On deployment of Balancing Energy Services, the QSE shall control its Resources to operate to the final Resource bilateral schedules as converted to a base power function plus the equivalent power requirement of the Balancing Energy Services Dispatch Instruction.  ERCOT calculation of SCE for each two (2) seconds and integrated over the Settlement Interval will indicate the average performance of the QSE to supply Balancing Energy Services.  Measurement of performance shall be accomplished using the SCE monitoring criteria described in Section 6.10.5.3, SCE Monitoring Criteria.

On deployment of BULs, the QSE shall control its Loads to the difference between its Scheduled power and the BUL instructed amount.  ERCOT, at a time established at its discretion, shall determine the base Load of the sum of all Loads qualified by the QSE as BUL Resources by obtaining actual meter data from IDR meters or directly from the TDSP who has agreed to Supply the data.  The base Load is determined by finding the average actual metered energy during the same interval as the instruction to deploy BUL from the previous ten (10) days (in the case of weekday deployment) or six (6) days (in the case of weekend or holiday deployment).  Days in which BUL instructions occurred during the same interval are ignored.  If the instruction to deploy occurs on a weekday, only weekdays are included in the average.  If the instruction to deploy occurs on a weekend, only weekend days and ERCOT-defined holidays are included in the average.

ERCOT shall also integrate for each Settlement Interval the signal provided by the QSE representing the amount of BUL power deployed.  The expected total reduction of Load shall be determined by subtracting the integrated signal for each interval from the base Load as determined above.  Control performance of the QSE providing BUL shall be deemed satisfactory when during the first hour in which BUL is deployed in an Operating Day, the actual metered Load for any Settlement Interval during the hour is equal to or less than the amount of energy expected.  Failure of the QSE to provide satisfactory control performance during the first hour in which BUL is deployed in an Operating Day will cause ERCOT to withhold payments for any capacity provided as BUL for the Operating Day.  Failure of a BUL to provide at least ninety percent (90%) of the expected total Load during the first hour of deployment for three (3) Operating Days in a year will disqualify a BUL.

The QSE will have to requalify the specific BUL; however, there will be a ninety (90) day waiting period before the BUL can be requalified.  To be requalified, the BUL will have to successfully reduce Load during the following BUL requalification test.  The QSE shall nominate to ERCOT the BUL which it wishes to requalify.  During a period of time mutually agreed to by the QSE and ERCOT, at a specific time selected by ERCOT, the ERCOT operator will notify the QSE that it wants to reverify the BUL’s ability to provide ERCOT with the appropriate Load reduction.  Upon receipt of the ERCOT Notification, the QSE Operator will immediately initiate the BUL reduction and provide ERCOT with the appropriate signal representing the amount of Load to be reduced.  Upon completion of the deployment interval, the ERCOT Testing Operator shall call the QSE and notify it that the test is complete.  At this time the deployed Resources may be restored to their normal state.

Load used to provide BUL Resources shall be requalified for correct operation by comparing the average energy in a Settlement Interval as recorded on IDR meters to the expected reduction in total Load indicated by the QSE’s signal to ERCOT.  Once ERCOT has verified that it actually received the committed Load reduction from the BUL, the QSE will be notified when the BUL can resume providing Balancing Up Energy Service.  If the BUL fails the requalification test, the QSE may request an additional requalification test for that BUL, but the BUL shall not be allowed to have more than three (3) requalification tests in a year.

[PRR311 and PRR484: Replace the above two paragraphs with the following upon system implementation:] On deployment of BULs, the QSE shall control its Loads to the difference between its scheduled power and the BUL instructed amount. ERCOT, at a time established at its discretion, shall determine the base Load of the sum of all Loads qualified by the QSE as BUL Resources by obtaining actual meter data from IDR meters, or from a sample of Loads controlled under a Direct Load Control (DLC) program qualified in accordance with Section 18.7.2, Load Profiling of ESI IDs Under Direct Load Control, or directly from the TDSP who has agreed to supply the data. While IDRs must normally be present on all Loads providing BUL Resources, IDRs may be installed and read on a sample of the Loads qualified by a QSE as a BUL Resource, provided the Loads are sampled in accordance with Section 18.7.2, Load Profiling of ESI IDs under Direct Load Control. Except in the case of a qualified DLC program, the base Load is determined by finding the average actual metered energy during the same interval as the instruction to deploy BUL from the previous ten (10) days (in the case of weekday deployment) or six (6) days (in the case of weekend or holiday deployment). In the case of a qualified DLC program, the base Load is the representative sample metered energy administered in accordance with Section 18.7.2, Load Profiling of ESI IDs Under Direct Load Control. Days in which BUL instructions occurred during the same interval are ignored. If the instruction to deploy occurs on a weekday, only weekdays are included in the average. If the instruction to deploy occurs on a weekend, only weekend days and ERCOT-defined holidays are included in the average. For small Customer Load management programs, base Load for each interval is determined from the aggregated appropriate baseline Load Profile for participating customers assuming the Load management program is not in operation. ERCOT shall also integrate, for each Settlement Interval, the signal provided by the QSE representing the amount of BUL power deployed. The expected total reduction of Load shall be determined by subtracting the integrated signal for each interval from the base Load as determined above. For small Customer Load management programs during each interval, the expected total reduction of Load shall be determined by subtracting the aggregated participating Customer Load during operation of the Load management program, which is calculated from the appropriate Load Profile, from the base Load for these customers as calculated above. Control performance of the QSE providing BUL shall be deemed satisfactory when during the first hour in which BUL is deployed in an Operating Day, the actual metered Load for any Settlement Interval during the hour is equal to or less than the amount of energy expected. Control performance of the QSE providing BUL through a qualified DLC program shall be deemed satisfactory when, during the first hour in which BUL is deployed in an Operating Day, the estimated actual Load developed from the representative sample administered in accordance with Section 18.7.2, Load Profiling of ESI IDs Under Direct Load Control, for any Settlement Interval during the hour is equal to or less than the amount of energy expected. Failure of the QSE to provide satisfactory control performance during the first hour in which BUL is deployed in an Operating Day will cause ERCOT to withhold payments for any capacity provided as BUL for the Operating Day. Failure of a BUL to provide at least ninety percent (90%) of the expected total Load during the first hour of deployment for three (3) Operating Days in a year will disqualify a BUL. The QSE will have to requalify the specific BUL; however, there will be a ninety (90) day waiting period before the BUL can be requalified. To be requalified, the BUL will have to successfully reduce Load during the following BUL requalification test. The QSE shall nominate to ERCOT the BUL which it wishes to requalify. During a period of time mutually agreed to by the QSE and ERCOT, at a specific time selected by ERCOT, the ERCOT operator will notify the QSE that it wants to reverify the BUL’s ability to provide ERCOT with the appropriate Load reduction. Upon receipt of the ERCOT Notification, the QSE Operator will immediately initiate the BUL reduction and provide ERCOT with the appropriate signal representing the amount of Load to be reduced. Upon completion of the deployment interval, the ERCOT Testing Operator shall call the QSE and notify it that the test is complete. At this time the deployed Resources may be restored to their normal state. Except in the case of a qualified DLC program, Load used to provide BUL Resources shall be requalified for correct operation by comparing the average energy in a Settlement Interval as recorded on IDR meters to the expected reduction in total Load indicated by the QSE’s signal to ERCOT. In the case of a qualified DLC program, the base Load is the average energy in a Settlement Interval developed from the representative sample administered in accordance with Section 18.7.2, Load Profiling of ESI IDs Under Direct Load Control. Once ERCOT has verified that it actually received the committed Load reduction from the BUL, the QSE will be notified when the BUL can resume providing Balancing Up Energy Service. If the BUL fails the requalification test, the QSE may request an additional requalification test for that BUL, but the BUL shall not be allowed to have more than three (3) requalification tests in a year.

6.10.5.3	SCE Monitoring Criteria

SCE Monitoring Criteria will be reviewed by the appropriate ERCOT TAC subcommittee and submitted into these Protocols upon approval.

Each QSE shall control its Resources to operate to the final Resource bilateral schedules as converted to a base power function plus the equivalent power requirement of any instructed Ancillary Services and other SCE obligation terms including governor response.  ERCOT shall calculate one (1) and ten (10) minute averages of each QSE’s SCE.  ERCOT shall also calculate each QSE’s participation factor as the ratio of the QSE’s generation scheduled change in the measurement period (1 or 10 minute) to the total ERCOT generation scheduled change in the same measurement period.  For performance monitoring purposes, ERCOT shall limit the deployment of RGS Service to QSEs for each control cycle equal to one hundred twenty five percent (125%) of the total amount of RGS Service in ERCOT divided by the number of control cycles in ten (10) minutes.  Intervals where a QSE’s generation is less than one (1) MW in the measurement period (1 or 10 minute) will not be included in the calculation of the SCE Monitoring Criteria.  Satisfactory control performance of the QSE shall be deemed acceptable when:

(1)	The one (1) minute averages of the QSE’s SCE meet the following criteria over the calendar month (commonly referred to as SCPS1), and

AVG(month)SCE1ParticipationFactor∗ΔF1(10∗Bias1)∗ε21≤1

(2)	The ten (10) minute averages of the QSE’s SCE meet the following criteria for ninety percent (90%) of the ten (10) minute periods over the calendar month (commonly referred to as SCPS2).

SCE10≤L10∗KParticipationFactor

Where:

SCE1 	is the one minute average of SCE.

SCE10	is the ten minute average of SCE.

Bias1 	is the one minute average of the ERCOT total bias used in the ACE calculation.

F1 	is the one minute average of frequency deviation from schedule.

Participation Factor	is determined by the ratio of the QSE’s generation scheduled change for the measurement period (1 or 10 minute) to total ERCOT generation schedule change for the measurement period (1 or 10 minute).  Generation schedule change per interval is defined as below:

{Absolute Value

[     (ResourceSchedule – ResourceSchedulePreviousInterval)

+ (BalancingDeployment – BalancingDeploymentPreviousInterval)  ]

+ RegulationUpSchedule

+ RegulationDownSchedule}

If this Participation Factor Calculation results in a value of less than 1%, then 1% will be used.

 	is a constant derived from the targeted frequency bound.  It is the targeted root-mean score of one (1) minute average frequency error from a schedule based on frequency performance over a given year as established according to NERC Performance Requirements by ERCOT and the appropriate ERCOT Subcommittee as assigned by TAC.

L10 	is a limit to recognize the desired performance of frequency for ERCOT as established according to NERC Performance Requirements by the appropriate ERCOT Subcommittee assigned by TAC.  As of July 2003, L10 is defined as (1.65 * E10 * 10 * Bias10) where E10 is 0.01315 Hz and Bias10 is the ten (10) minute average of the ERCOT total bias used in the ACE calculation.

K	is a constant currently set to .81 which is established by the appropriate ERCOT Subcommittee as assigned by TAC.  K should initially be set to .81 to provide an ERCOT wide L10 equivalent to the ERCOT wide L10 currently used by Control Areas in ERCOT.  This constant can be adjusted to ensure correlation between passing the NERC CPS2 criteria and passing the SCE ten (10) minute control limit.

6.10.5.4	Responsive Reserve Services Performance Monitoring Criteria

QSEs providing Responsive Reserve Services must so indicate in the Scheduling Process.  QSEs shall have Resources available to meet the schedule while adhering to the Responsive Reserve Service requirements detailed in the Operating Guides. On deployment of any Responsive Reserve Service, the QSE shall control its Resources to operate to the final Resource bilateral schedules as converted to a base power function plus the instructed Responsive Reserve Service power requirement.  ERCOT’s calculation of SCE ten (10) minutes after the deployment instruction will determine the level of Responsive Reserve Service provided.  Satisfactory control performance of the QSE providing only Responsive Reserve Services shall be deemed satisfactory when:

(1)	Not less than ninety-five percent (95%) nor more than one hundred fifty percent (150%) of the RRS requested, subject to the declared capabilities of the QSE, is provided within ten (10) minutes of ERCOT’s deployment Dispatch Instruction and maintained until recalled or the QSEs service Obligation expires; and

(2)	Generation Resources providing the RRS requested shall return to within ninety percent (90%) to one hundred ten percent (110%) of their pre-deployment scheduled output, subject to the declared capabilities of the QSE, within ten (10) minutes following a recall instruction from ERCOT.  LaaRs providing the RRS requested shall return to their committed operating level for providing RRS service as soon as practical considering process constraints. For LaaRs unable to return to their committed operating level within three (3) hours, their QSE may schedule the quantity of deficient Responsive Reserve Service Capacity from other uncommitted Generation or LaaR Resource(s) to satisfy the control performance requirement described in this Section.

[PRR502: Add the following item to Section 6.10.5.4, item (3) upon system implementation:] (3) RRS bids from QSEs may include contributions from combined cycle Resources in Aggregated Units meeting the criteria in Section 6.8.2.4, Aggregating Units. Thus, to determine if a combined cycle Aggregated Unit is capable of performing its RRS Obligation, all Resources On-line in the Aggregated Unit will be measured as on an aggregate capacity basis and will be calculated from the lower of the High Sustainable Limits specified in the Resource Plan or through telemetry, or the seasonal tested Net Dependable Capability.

For all frequency deviations exceeding 0.175 Hz, ERCOT shall measure and record each two (2) second scan rate values of real power output for each QSE Resource providing Responsive Reserve Service.  ERCOT shall measure and record the MW data beginning one (1) minute prior to the start of the frequency excursion event or Manual / Dispatch Instruction until ten (10) minutes after the start of the frequency excursion event or Manual / Dispatch Instruction.  Satisfactory performance is measured by comparing the actual response to the frequency response capability required in the Operating Guides.

Where multiple observations of operating response are available, the QSE must deliver the required frequency response capability seventy-five percent (75%) of the time during any single calendar quarter.

6.10.5.5	Non-Spinning Reserve Services Performance Monitoring Criteria

QSEs providing Non-Spinning Reserve Services must so indicate in the Scheduling Process.  On deployment of any Non-Spinning Reserve Service, the QSE shall control its Resources to operate to the final Resource bilateral schedules as converted to a base power function plus the instructed Non-Spinning Reserve power requirement.  ERCOT’s calculation of SCE thirty (30) minutes after the Dispatch Instruction will determine the level of Non-Spinning Reserve provided.  Control performance of the QSE providing only Non-Spinning Reserve Services shall be deemed satisfactory when:

(1)	Not less than ninety-five percent (95%) nor more than one hundred fifty percent (150%) of the Non-Spinning Reserve Services requested, subject to the declared capabilities of the QSE, is provided within thirty (30) minutes of ERCOT’s deployment Dispatch Instruction and maintained until recalled or the QSE’s service Obligation expires; and,

(2)	The Non-Spinning Reserve Service requested shall return to within ninety percent (90%) to one hundred ten percent (110%) of its pre-deployment scheduled output, subject to the declared capabilities of the QSE, within thirty (30) minutes following a recall instruction from ERCOT, or as soon as practical considering process constraints if the Non-Spinning Reserve Service is being served by a LaaR.

[PRR436: Add the following to Section 6.10.5.5, item (2) upon system implementation:] (a) During periods when the Load level of a LaaR has been affected by a Dispatch Instruction from ERCOT, the performance of a LaaR in response to a Dispatch Instruction will be determined by subtracting the LaaR’s actual Load response from its baseline. The actual Load response is the average of the real power consumption data being telemetered to ERCOT during the Settlement Interval indicated in the Dispatch Instruction. The baseline capacity is calculated by measuring the average of the real power consumption for the four (4) Settlement Intervals prior to the Dispatch Instruction. During hours when the Load level of a LaaR has not been affected by a Dispatch Instruction from ERCOT, the Resource quantity provided by the LaaR scheduled or selected by ERCOT to provide Non-Spinning Reserve Service shall be measured as the LaaR’s average Load level during the hour.

6.10.5.6	Combinations of Reliability Services Monitoring Criteria

QSEs providing any combination of services shall control their Resources to the additive result of any number of Dispatch Instructions deployed simultaneously.  On deployment of any Balancing Energy, Regulation, Responsive Reserve, and Non-Spinning Reserve Service, the QSE shall control its Resources to operate to the final Resource bilateral schedules as converted to a base power function plus the additive power requirement of each effective Dispatch Instruction.  Satisfactory control performance of the QSE providing any combination of services will be determined by a combination of the following:

(1)	The criteria for SCE Monitoring at all times with exclusions as noted in Section 6.10.6; and

(2)	The criteria for Responsive Reserve if Responsive Reserve Service is one of the services deployed; and

(3)	The criteria for Non-Spinning Reserve Service if Non-Spinning is one of the services deployed.

6.10.6	Ancillary Service Deployment Performance Conditions

ERCOT shall determine the performance of providers of QSE SCE Performance under normal operating conditions.  ERCOT shall remove from consideration of average performance of a QSE any period during which any of the following events has occurred and which does not have a passing score.

(1)	The two (2) hour period after the QSE has experienced a Forced Outage;

(2)	The entire Settlement Intervals for all QSEs in which ERCOT has deployed or recalled Balancing Energy in response to an Unusual Event;

(3)	The entire Settlement Intervals in which ERCOT has issued a verbal Dispatch Instruction;

(4)	The period where ERCOT issues instructions to any QSE to be deployed at ramp rates in excess of bid ramp rates such as the ten (10) minute time period where a QSE is ramping up due to a RRS deployment;

(5)	The entire Settlement Interval(s) in which a QSE is ramping into (from time of notification to time of deployment) or out of (from end of deployment to thirty (30) minutes later) a NSRS deployment; and

PIP112: Add item #6 below to the list and renumber the existing (6) to (7) when BUL is implemented: (6) If requested by a QSE, up to three (3) scheduling hours following an instruction issued by ERCOT to recall previously deployed Responsive Reserve, Non-Spin or Balancing Energy Up Services provided from Replacement Capacity that is using qualified Load as the QSE’s Resource; and

(6)	Certain other periods of abnormal operations as determined by ERCOT.

6.10.7	Individual Resource Dispatch Performance

QSEs may receive Dispatch Instructions to operate a specific Resource within limitations specified for an individual Resource.  The QSE shall conform to the limitations restricting Resource loading for the effective time of the Dispatch Instruction to within two (2) MW of the requested limitation.

6.10.8	Replacement Reserve and OOMC Service Performance Criteria

QSEs awarded Replacement Reserve or OOMC Service to bring a Generation Resource unit On-line or make available LaaR for Replacement Reserve Service shall make a good faith effort to cause their Resources to be available for required Balancing Energy instructions at the time requested by ERCOT.  Any QSE that anticipates for any reason it may not be able to honor its commitment because of unexpected problems shall notify ERCOT immediately.  ERCOT will monitor the Real Time telemetry of the subject Resource breakers and megawatt output to determine if it is available as purchased.  Performance shall be satisfactory if the Resource is brought On-line or made available and the QSE makes available required Balancing Energy bids, which, for a LaaR, is at least in the amount of the capacity of the awarded Resource, and, for an awarded Generation Resource, is the High Sustainable Limit minus the Low Sustainable Limit throughout the period requested.  QSEs failing to bring the Generation Resource On-line or make the LaaR active shall not be entitled to compensation for the intervals that the capacity was not available.  QSEs failing to provide the required levels of Balancing Energy bids in response to the awards shall not be entitled to compensation for that amount of capacity not made available.

[PRR436: Replace Section 6.10.8 with the following upon system implementation:] QSEs awarded Replacement Reserve or OOMC Service to bring a Generation Resource unit On-line or make available LaaR for Replacement Reserve Service shall make a good faith effort to cause their Resources to be available for required Balancing Energy instructions at the time requested by ERCOT. Any QSE that anticipates for any reason it may not be able to honor its commitment because of unexpected problems shall notify ERCOT immediately. ERCOT will monitor the Real Time telemetry of the subject Resource breakers and megawatt output to determine if it is available as purchased. Performance shall be satisfactory if the Resource is brought On-line or made available and the QSE makes available required Balancing Energy bids, which, for a LaaR, is at least in the amount of the capacity of the awarded Resource, and, for an awarded Generation Resource, is the High Sustainable Limit minus the Low Sustainable Limit throughout the period requested. During periods when the Load level of a LaaR has been affected by a Dispatch Instruction from ERCOT, the performance of a LaaR in response to a Dispatch Instruction will be determined by subtracting the LaaR’s actual Load response from its baseline. The actual Load response is the average of the real power consumption data being telemetered to ERCOT during the Settlement Interval indicated in the Dispatch Instruction. The baseline capacity is calculated by measuring the average of the real power consumption for the four (4) Settlement Intervals prior to the Dispatch Instruction. During hours when the Load level of a LaaR has not been affected by a Dispatch Instruction from ERCOT, the Resource quantity provided by a LaaR scheduled or selected by ERCOT to provide Replacement Reserves shall be measured as the LaaR’s average Load level during the hour. QSEs failing to bring the Generation Resource On-line or make the LaaR active shall not be entitled to compensation for the intervals that the capacity was not available. QSEs failing to provide the required levels of Balancing Energy bids in response to the awards shall not be entitled to compensation for that amount of capacity not made available.

6.10.9	Reactive Power Supply from Generation Resources Required to Provide VSS Performance Criteria

(1)	ERCOT will maintain a performance log of QSEs acknowledgements of Dispatch Instructions concerning scheduled voltage or scheduled Reactive output requests.  QSEs responding in less than two (2) minutes from the time of issuance of such requests shall be deemed satisfactory.

(2)	ERCOT shall monitor the Automatic Voltage Regulator, as required in Section 6.5.7, Voltage Support Service, to assure that it is on and operating automatically at least ninety-eight percent (98%) of the time in which the QSE is providing the Reactive Power Supply from Generation Resources required to provide VSS.  The percentage is calculated as:  Time (Automatic Voltage Regulator is on while providing Service) / (Total Time Providing Services)  100%.

(3)	Except under Force Majeure conditions or ERCOT-permitted operation of the generating unit, failure of a Generation Resource required to provide VSS to provide either leading or lagging reactive up to the required capability of the unit upon request from a TSP or ERCOT may, at the discretion of ERCOT, be reported to the ERCOT Compliance Office.

(4)	Except under Force Majeure conditions or ERCOT-permitted operation of the generating unit, if a Generation Resource required to provide VSS fails to maintain transmission system voltage at the point of interconnection with the TSP within two percent (2%) of the scheduled voltage while operating at less than the maximum reactive capability of the generating unit, ERCOT may, at its discretion, report this to the ERCOT Compliance Office.

(5)	The ERCOT Compliance Office will investigate claims of alleged non-compliance and Force Majeure conditions, and address confirmed non-compliance situations.  The ERCOT Compliance Office will advise the Generation Resource, its QSE, ERCOT, and the TSP planning and operating staffs of the results of such investigations.

6.10.10	System Black Start Capability Performance Criteria

The Black Start Unit shall maintain qualified System Black Start Capability, with the declared capacity and capabilities of the Resources continuously; except during those periods allowed for routine maintenance.  During a system restoration emergency, the provider shall respond to the instructions of ERCOT, subject to the declared capacity and capabilities of the system Black Start Capability Generation Resources.

The Black Start Resource shall complete all initial and ongoing qualification requirements.

6.10.11	ERCOT Operations Performance

(1)	ERCOT shall continuously self-assess its operations and report to all Market Participants its performance in controlling the ERCOT Control Area according to requirements and criteria established by the Operating Guides and NERC Policy and Standards for operation of Control Areas.  ERCOT shall report all substandard operations to the ERCOT Technical Advisory Committee and to the NERC Compliance and Enforcement Committees.

(2)	ERCOT shall publish for all Market Participants the total amount of Regulation Up energy deployed and the total amount of Regulation Down energy deployed in each Settlement Interval.

(3)	ERCOT shall provide monthly a report analyzing the accuracy of each Operating Day’s Load forecast that was issued at 0600 the Day Ahead of the Operating Day.  ERCOT shall make similar comparisons for the 1100 forecast and the forecast in effect at midnight of the start of the Operating Day.  In its reports, ERCOT shall statistically analyze the expected error in energy and peak forecasting.

(4)	ERCOT shall publish for all Market Participants the percentage of the Bid Stack awarded for Balancing Energy Service for each Settlement Interval that ERCOT deploys any Non-Spinning Reserve Service.

(5)	ERCOT shall provide a monthly report showing the average percentage of the Bid Stack award for Balancing Energy Service for the Settlement Intervals that ERCOT deploys Non-Spinning Reserve Service for the month.

6.10.12	Non-Compliance Actions of ERCOT

ERCOT may revoke any or all Ancillary Service qualification of any QSE providing an Ancillary Service(s) for continued under-performance.

Failure to deliver energy resulting from a valid Dispatch Instruction is cause for ERCOT, at ERCOT’s option, to withhold payment for any Ancillary Services purchased and not delivered.

ERCOT will make information relative to each QSE’s performance as well as ERCOT’s performance, available to the marketplace on a monthly basis, subject to the provisions of Section 1.3.1, Restrictions on Protected Information.

In this case, only QSE’s that overgenerate would be subject to the uninstructed charge when the price is greater than the benchmarked costs.