1. Distribution loss factor calculation from ERCOT Protocols section 13.3.1.1:

SILFi= ADLF ∗K +1 - K∗SIELiAAL

Where:

i	=  settlement interval

SILFi	=  Settlement Interval Distribution Loss Factor

ADLF 	=  Annual Distribution Loss factor

K	=  a factor provided by DSP between 0.0 and 0.1

SIELi	=  Settlement Interval estimated ERCOT System Load

AAL	=  Annual Interval Average ERCOT System Load

- Settlement Interval Losses

Total losses at a give system load are equal to a “no-load” loss component which does not vary with system load, plus a “load” loss component which varies with the square of the system load.


SILi=NLL + ALL∗SIELiAAL2

Where:

	NLL	=  No load losses

	ALL	=  Average load losses (at average system load AAL)

- Total losses at Annual Interval Average ERCOT System Load

 
ADL=NLL + ALL

Where:

	ADL	=  Total losses at Annual Interval Average ERCOT System Load

- Substituting:
SILi=NLL +ADL−NLL∗SIELiAAL2

- Multiply by ADL / ADL: 
SILi=ADL∗NLLADL+ADL−NLLADL∗SIELiAAL2

- Definition of K factor:

K is the fraction of losses at average load due to “no-load” losses.

K=NLLADL

- Substituting:
SILi=ADL∗K +1−K∗SIELiAAL2

- Calculate loss factor:
SILFi=SILiSIELi=ADLSIELi∗K +1−K∗SIELiAAL2

- SILFi=ADLAAL∗AALSIELi∗K +1−K∗SIELiAAL2

- Assume:
ADLF=ADLAAL

- Substitute:
SILFi=ADLF∗K∗AALSIELi+1−K∗SIELiAAL

This is what the equation for SILFi ought to be.

- Assume K = 0 (no-load losses equal to zero):
SILFi=ADLF∗0∗AALSIELi+1−0∗SIELiAAL
or
SILFi=ADLF∗SIELiAAL

This gives the same result as the equation in the ERCOT protocols.

- Assume K=1 (losses are constant):
SILFi=ADLF∗1∗AALSIELi+1−1∗SIELiAAL
or
SILFi=ADLF∗AALSIELi
This is not the same result as the equation in the ERCOT protocols. The equation in the protocols is a constant when K = 1, this equation is a hyperbola.